## All Data
|  |  |  | X1 | X2 | X3 | X4 | X5 | X6 | X7 | X8 | X9 | X10 | X11 | X12 | X13 | Y1 | Z1 | Z2 | Z3 | Y2
|  |  |  | Voc |  | Ib | X/R |  | Eg | Eb | D |  | Bs | Bd |  |  | Ia | Va
Entry | Test Set | Test item | Test Number | Open Circuit Voltage ph-ph (kV) | System Grounded -- Y, N, HRG | Bolted fault current (kA) | X/R Ratio | Electrode material SS, AL, CH, CS | Gap between electrodes (mm) | Gap electrodes to box (mm) | Distance from arc to calorimeters (mm) | Arc Duration (msec) | Box width + height/2 (mm) | Box depth (mm) | No. of phases | Electrode configuration (Parallel or Inline) | Arc Current (kA) | Arc Voltage L-L (kV) | Arc energy (kj) | Incident energy, the mean of 7 calorimeters (cal/cm²) | Incident energy, the max of 7 calorimeters (cal/cm²)
1 | Paper 97-35 | 1 | 3 test averages | 0.61 | N | 36.25 |  | CH | 31.8 | 10000 | 600 | 100 | 10000 | 10000 | 3 | D | 19.93 | 0.3227 | 1296.3 |  | 1.2015
2 | Paper 97-35 | 2 | 3 test averages | 0.61 | N | 36.25 |  | CH | 50.8 | 10000 | 600 | 100 | 10000 | 10000 | 3 | Delta | 14.12 | 0.3384 | 879.1 |  | 1.161
3 | Paper 97-35 | 3 | 3 test averages | 0.61 | N | 36.25 |  | CH | 19.1 | 10000 | 600 | 100 | 10000 | 10000 | 3 | Parallel | 25.52 | 0.2479 | 1303.6 |  | 2.025
4 | Paper 97-35 | 4 | 3 test averages | 0.61 | N | 36.25 |  | CH | 25.4 | 10000 | 600 | 100 | 10000 | 10000 | 3 | Parallel | 24.23 | 0.2679 | 1367.6 |  | 1.9035
5 | Paper 97-35 | 5 | 3 test averages | 0.61 | N | 36.25 |  | CH | 31.8 | 10000 | 600 | 100 | 10000 | 10000 | 3 | Parallel | 22.12 | 0.2842 | 1342.6 |  | 2.2005
6 | Paper 97-35 | 6 | 3 test averages | 0.61 | N | 36.25 |  | CH | 50.8 | 10000 | 600 | 100 | 10000 | 10000 | 3 | Parallel | 17.79 | 0.3276 | 1234.6 |  | 1.917
7 | Paper 97-35 | 7 | 3 test averages | 0.61 | N | 36.25 |  | CH | 76.2 | 10000 | 600 | 100 | 10000 | 10000 | 3 | Parallel | 11.76 | 0.3648 | 849.2 |  | 1.2285
8 | Paper 97-35 | 8 | 3 test averages | 0.61 | N | 36.25 |  | CH | 19.1 | 102 | 600 | 100 | 10000 | 10000 | 3 | Parallel | 24.9 | 0.2682 | 1413.9 |  | 1.7955
9 | Paper 97-35 | 9 | 3 test averages | 0.61 | N | 36.25 |  | CH | 25.4 | 102 | 600 | 100 | 10000 | 10000 | 3 | Parallel | 24.67 | 0.2655 | 1403.5 |  | 2.268
10 | Paper 97-35 | 10 | 3 test averages | 0.61 | N | 36.25 |  | CH | 31.8 | 102 | 600 | 100 | 10000 | 10000 | 3 | Parallel | 22.82 | 0.3015 | 1444 |  | 2.322
11 | Paper 97-35 | 11 | 3 test averages | 0.61 | N | 36.25 |  | CH | 31.8 | 102 | 600 | 100 | 533.4 | 533.4 | 3 | Parallel | 28.67 | 0.2126 | 1174.1 |  | 6.966
12 | Paper Vol 36-1 | 1 | 4 test averages | 0.768 | N | 50.39 |  | CH | 32 | 10000 | 610 | 100 | 10000 | 10000 | 3 | Parallel | 34.88 | 0.5289 | 2306.1 | 3.71 | 4.63
13 | Paper Vol 36-1 | 2 | 4 test averages | 0.687 | N | 45.36 |  | CH | 32 | 10000 | 610 | 100 | 10000 | 10000 | 3 | Parallel | 30.15 | 0.4658 | 1638.6 | 2.98 | 3.87
14 | Paper Vol 36-1 | 3 | 4 test averages | 0.614 | N | 40.92 |  | CH | 32 | 10000 | 610 | 100 | 10000 | 10000 | 3 | Parallel | 24.08 | 0.4716 | 1358.3 | 2.46 | 2.96
15 | Paper Vol 36-1 | 4 | 4 test averages | 0.616 | N | 35.29 |  | CH | 32 | 10000 | 610 | 100 | 10000 | 10000 | 3 | Parallel | 22.3 | 0.4612 | 1217.9 | 2.31 | 2.52
16 | Paper Vol 36-1 | 5 | 4 test averages | 0.623 | N | 31.16 |  | CH | 32 | 10000 | 610 | 100 | 10000 | 10000 | 3 | Parallel | 20.99 | 0.4326 | 1090.2 | 2.05 | 2.3
17 | Paper Vol 36-1 | 6 | 4 test averages | 0.617 | N | 27.66 |  | CH | 32 | 10000 | 610 | 100 | 10000 | 10000 | 3 | Parallel | 18.74 | 0.4392 | 1004.6 | 1.8 | 1.97
18 | Paper Vol 36-1 | 7 | 4 test averages | 0.614 | N | 23.41 |  | CH | 32 | 10000 | 610 | 100 | 10000 | 10000 | 3 | Parallel | 16.44 | 0.4428 | 920.4 | 1.49 | 1.78
19 | Paper Vol 36-1 | 8 | 4 test averages | 0.615 | N | 19.08 |  | CH | 32 | 10000 | 610 | 100 | 10000 | 10000 | 3 | Parallel | 13.27 | 0.4431 | 701.8 | 1.1 | 1.25
20 | Paper Vol 36-1 | 9 | 4 test averages | 0.616 | N | 16.3 |  | CH | 32 | 10000 | 610 | 100 | 10000 | 10000 | 3 | Parallel | 11.58 | 0.4542 | 619.3 | 0.94 | 1.1
21 | Paper Vol 36-1 | 10 | 4 test averages | 0.614 | N | 40.92 |  | CH | 32 | 10000 | 457 | 100 | 10000 | 10000 | 3 | Parallel | 25.47 | 0.4495 | 1350.9 | 4.63 | 5.52
22 | Paper Vol 36-1 | 11 | 4 test averages | 0.614 | N | 40.92 |  | CH | 32 | 10000 | 762 | 100 | 10000 | 10000 | 3 | Parallel | 25.44 | 0.4454 | 1373.5 | 1.86 | 2.04
23 | Paper Vol 36-1 | 12 | 4 test averages | 0.759 | N | 51.19 |  | CH | 32 | 102 | 610 | 100 | 508 | 508 | 3 | Parallel | 41.15 | 0.375 | 1757.8 | 9.4 | 12.46
24 | Paper Vol 36-1 | 13 | 4 test averages | 0.68 | N | 46.05 |  | CH | 32 | 102 | 610 | 100 | 508 | 508 | 3 | Parallel | 36.33 | 0.3434 | 1437.5 | 7.41 | 9.85
25 | Paper Vol 36-1 | 14 | 4 test averages | 0.612 | N | 41.99 |  | CH | 32 | 102 | 610 | 100 | 508 | 508 | 3 | Parallel | 31.59 | 0.3403 | 1266.4 | 5.16 | 8.01
26 | Paper Vol 36-1 | 15 | 4 test averages | 0.618 | N | 36.25 |  | CH | 32 | 102 | 610 | 100 | 508 | 508 | 3 | Parallel | 27.31 | 0.3505 | 1122.2 | 3.76 | 5.4
27 | Paper Vol 36-1 | 16 | 4 test averages | 0.613 | N | 31.2 |  | CH | 32 | 102 | 610 | 100 | 508 | 508 | 3 | Parallel | 24.92 | 0.3297 | 970.9 | 2.97 | 4.01
28 | Paper Vol 36-1 | 17 | 4 test averages | 0.617 | N | 27.66 |  | CH | 32 | 102 | 610 | 100 | 508 | 508 | 3 | Parallel | 21.9 | 0.3277 | 844.2 | 2.87 | 3.63
29 | Paper Vol 36-1 | 18 | 4 test averages | 0.611 | N | 23.65 |  | CH | 32 | 102 | 610 | 100 | 508 | 508 | 3 | Parallel | 19.01 | 0.3237 | 743.9 | 2.32 | 2.96
30 | Paper Vol 36-1 | 19 | 4 test averages | 0.615 | N | 19.08 |  | CH | 32 | 102 | 610 | 100 | 508 | 508 | 3 | Parallel | 15.57 | 0.2448 | 602.3 | 1.91 | 3.1
31 | Paper Vol 36-1 | 20 | 4 test averages | 0.616 | N | 16.3 |  | CH | 32 | 102 | 610 | 100 | 508 | 508 | 3 | Parallel | 13.24 | 0.3177 | 505 | 1.67 | 2.55
32 | Paper Vol 36-1 | 21 | 4 test averages | 0.612 | N | 41.99 |  | CH | 32 | 102 | 457 | 100 | 508 | 508 | 3 | Parallel | 31.36 | 0.3474 | 1257.1 | 9.35 | 12.06
33 | Paper Vol 36-1 | 22 | 4 test averages | 0.612 | N | 41.99 |  | CH | 32 | 102 | 762 | 100 | 508 | 508 | 3 | Parallel | 32.12 | 0.3265 | 1227.5 | 4.13 | 5.03
34 | Paper Vol 36-1 | 23 | 4 test averages | 0.612 | N | 41.99 |  | CH | 32 | 102 | 914 | 100 | 508 | 508 | 3 | Parallel | 32.15 | 0.3254 | 1187.1 | 3.15 | 4.24
35 | Paper Vol 36-1 | 24 | 4 test averages | 0.612 | N | 41.99 |  | CH | 32 | 102 | 1219 | 100 | 508 | 508 | 3 | Parallel | 31.79 | 0.3316 | 1243 | 1.81 | 2.73
36 | Paper Vol 36-1 | 25 | 4 test averages | 0.612 | N | 41.99 |  | CH | 32 | 102 | 1524 | 100 | 508 | 508 | 3 | Parallel | 32.16 | 0.3282 | 1224.5 | 1.05 | 2.08
37 | CLF Paper | 1 | multiple test avgs | 0.6 | N | 106 | 7.9 | CH | 32 | 102 | 448 | 100 | 508 | 508 | 3 | Parallel | 45.98 |  | 4205 | 22.42 | 35.71
38 | CLF Paper | 1 | multiple test avgs | 0.6 | N | 65.9 | 9.95 | CH | 32 | 102 | 448 | 100 | 508 | 508 | 3 | Parallel | 36.77 |  | 2918 | 16.21 | 21.29
39 | CLF Paper | 1 | multiple test avgs | 0.6 | N | 44.1 | 11 | CH | 32 | 102 | 448 | 100 | 508 | 508 | 3 | Parallel | 25.97 |  | 1433 | 12.23 | 15.68
40 | CLF Paper | 1 | multiple test avgs | 0.6 | N | 22.6 | 4.9 | CH | 32 | 102 | 448 | 100 | 508 | 508 | 3 | Parallel | 15.8 |  | 875 | 5.93 | 7.79
41 | Kinectrics 2001 | 1 | "01-2297" | 0.6 | N | 0.671 | 40 | CH | 32 | 102 | 610 | 2060 | 508 | 508 | 3 | Parallel | 0.603 |  |  |  | 1.3
42 | Kinectrics 2001 | 1 | "01-2298" | 0.6 | N | 0.671 | 40 | CH | 32 | 102 | 610 | 2060 | 508 | 508 | 3 | Parallel | 0.615 | 0.28232 | 568 |  | 1.2
43 | Kinectrics 2001 | 1 | "01-2299" | 0.6 | N | 0.671 | 40 | CH | 32 | 102 | 610 | 2060 | 508 | 508 | 3 | Parallel | 0.613 | 0.3083 | 589 |  | 1.2
44 | Kinectrics 2001 | 1 | "01-2300" | 0.6 | N | 0.671 | 40 | CH | 32 | 102 | 610 | 2060 | 508 | 508 | 3 | Parallel | 0.624 | 0.27885 | 571 |  | 1.2
45 | Kinectrics 2001 | 1 | "01-2304" | 0.6 | N | 3.478 | 25 | CH | 32 | 102 | 610 | 2037 | 508 | 508 | 3 | Parallel | 2.992 | 0.33081 | 3123 |  | 23.5
46 | Kinectrics 2001 | 1 | "01-2305" | 0.6 | N | 3.478 | 25 | CH | 32 | 102 | 610 | 2037 | 508 | 508 | 3 | Parallel | 3.053 | 0.32562 | 3150 |  | 18.5
47 | Kinectrics 2001 | 1 | "01-2306" | 0.6 | N | 3.478 | 25 | CH | 32 | 102 | 610 | 2037 | 508 | 508 | 3 | Parallel | 3.022 | 0.33081 | 3097 |  | 17
48 | Kinectrics 2001 | 11 | "01-2330" | 0.59 | Y | 3.35 | 25 | CH | 10 | 10 | 610 | 805 | 508 | 508 | 3 | Parallel | 3.133 | 0.24075 | 963 |  | 7
49 | Kinectrics 2001 | 11 | "01-2331" | 0.59 | Y | 3.35 | 25 | CH | 10 | 10 | 610 | 805 | 508 | 508 | 3 | Parallel | 3.156 | 0.24941 | 947 |  | 7
50 | Kinectrics 2001 | 11 | "01-2332" | 0.59 | Y | 3.35 | 25 | CH | 10 | 10 | 610 | 805 | 508 | 508 | 3 | Parallel | 3.145 | 0.23728 | 928 |  | 6.9
51 | Kinectrics 2001 | 12 | "01-2333" | 0.59 | N | 3.35 | 25 | CH | 40 | 10 | 610 | 203 | 508 | 508 | 3 | Parallel | 2.833 | 0.31176 | 287 |  | 1.7
52 | Kinectrics 2001 | 12 | "01-2334" | 0.59 | N | 3.35 | 25 | CH | 40 | 10 | 610 | 203 | 508 | 508 | 3 | Parallel | 2.828 | 0.30656 | 279 |  | 1.7
53 | Kinectrics 2001 | 12 | "01-2335" | 0.59 | N | 3.35 | 25 | CH | 40 | 10 | 610 | 210 | 508 | 508 | 3 | Parallel | 2.818 | 0.2979 | 280 |  | 1.4
54 | Kinectrics 2001 | 13 | "01-2336" | 0.59 | Y | 3.35 | 25 | CH | 40 | 102 | 610 | 210 | 508 | 508 | 3 | Parallel | 2.582 | 0.42954 | 344 |  | 1.7
55 | Kinectrics 2001 | 13 | "01-2337" | 0.59 | Y | 3.35 | 25 | CH | 40 | 102 | 610 | 203 | 508 | 508 | 3 | Parallel | 2.584 | 0.40702 | 335 |  | 1.4
56 | Kinectrics 2001 | 13 | "01-2338" | 0.59 | Y | 3.35 | 25 | CH | 40 | 102 | 610 | 209 | 508 | 508 | 3 | Parallel | 2.546 | 0.44166 | 344 |  | 1.4
57 | Kinectrics 2001 | 14 | "01-2339" | 0.59 | N | 3.35 | 25 | CH | 10 | 102 | 610 | 808 | 508 | 508 | 3 | Parallel | 3.162 | 0.24075 | 941 |  | 4.3
58 | Kinectrics 2001 | 14 | "01-2340" | 0.59 | N | 3.35 | 25 | CH | 10 | 102 | 610 | 808 | 508 | 508 | 3 | Parallel | 3.15 | 0.24594 | 932 |  | 4.6
59 | Kinectrics 2001 | 14 | "01-2341" | 0.59 | N | 3.35 | 25 | CH | 10 | 102 | 610 | 808 | 508 | 508 | 3 | Parallel | 3.175 | 0.24075 | 957 |  | 5
60 | Kinectrics 2001 | 18B | "01-2344" | 0.59 | N | 30 | 6.5 | CH | 10 | 102 | 610 | 597 | 508 | 508 | 3 | Parallel | 24.194 |  |  |  | 19.3
61 | Kinectrics 2001 | 18B | "01-2345" | 0.59 | N | 30 | 6.5 | CH | 10 | 102 | 610 | 597 | 508 | 508 | 3 | Parallel | 24.08 |  |  |  | 22
62 | Kinectrics 2001 | 18B | "01-2346" | 0.59 | N | 30 | 6.5 | CH | 10 | 102 | 610 | 597 | 508 | 508 | 3 | Parallel | 24.712 |  |  |  | 18.1
63 | Kinectrics 2001 | 17 | "01-2347" | 0.59 | N | 30 | 6.5 | CH | 40 | 102 | 610 | 96 | 508 | 508 | 3 | Parallel | 21.068 | 0.3516 | 1104 |  | 3.4
64 | Kinectrics 2001 | 17 | "01-2348" | 0.59 | N | 30 | 6.5 | CH | 40 | 102 | 610 | 96 | 508 | 508 | 3 | Parallel | 21.204 | 0.3412 | 1068 |  | 3.2
65 | Kinectrics 2001 | 17 | "01-2349" | 0.59 | N | 30 | 6.5 | CH | 40 | 102 | 610 | 96 | 508 | 508 | 3 | Parallel | 21.649 | 0.33428 | 1065 |  | 3.1
66 | Kinectrics 2001 | 18 | "01-2350" | 0.59 | N | 30 | 6.5 | CH | 10 | 102 | 610 | 495 | 508 | 508 | 3 | Parallel | 24.694 | 0.23728 | 4857 |  | 15.1
67 | Kinectrics 2001 | 18 | "01-2351" | 0.59 | N | 30 | 6.5 | CH | 10 | 102 | 610 | 166 | 508 | 508 | 3 | Parallel | 24.531 | 0.22862 | 1590 |  | 4.3
68 | Kinectrics 2001 | 18 | "01-2352" | 0.59 | Y | 30 | 6.5 | CH | 10 | 102 | 610 | 172 | 508 | 508 | 3 | Parallel | 24.503 | 0.24421 | 1714 |  | 5
69 | Kinectrics 2001 | 18 | "01-2353" | 0.59 | Y | 30 | 6.5 | CH | 10 | 102 | 610 | 166 | 508 | 508 | 3 | Parallel | 24.544 | 0.23382 | 1618 |  | 5
70 | Kinectrics 2001 | 15 | "01-2354" | 0.59 | N | 30 | 6.5 | CH | 10 | 10 | 610 | 164 | 508 | 508 | 3 | Parallel | 24.746 | 0.61486 | 1696 |  | 7.8
71 | Kinectrics 2001 | 15 | "01-2355" | 0.59 | N | 30 | 6.5 | CH | 10 | 10 | 610 | 169 | 508 | 508 | 3 | Parallel | 24.679 | 0.24421 | 1680 |  | 7.7
72 | Kinectrics 2001 | 15 | "01-2356" | 0.59 | N | 30 | 6.5 | CH | 10 | 10 | 610 | 169 | 508 | 508 | 3 | Parallel | 24.213 | 0.25634 | 1729 |  | 9.1
73 | Kinectrics 2001 | 16 | "01-2359" | 0.59 | Y | 30 | 6.5 | CH | 40 | 10 | 610 | 169 | 508 | 508 | 3 | Parallel | 21.776 | 0.33081 | 1911 |  | 8.8
74 | Kinectrics 2001 | 16 | "01-2360" | 0.59 | Y | 30 | 6.5 | CH | 40 | 10 | 610 | 160 | 508 | 508 | 3 | Parallel | 22.18 | 0.32215 | 1857 |  | 8.2
75 | Kinectrics 2001 | 16 | "01-2361" | 0.59 | Y | 30 | 6.5 | CH | 40 | 10 | 610 | 160 | 508 | 508 | 3 | Parallel | 22.326 | 0.31869 | 1840 |  | 8.4
84 | Kinectrics 2001 | 25E | "01-2370" | 0.25 | Y | 20 | 7 | CH | 10 | 10 | 610 | 230 | 508 | 508 | 3 | Parallel | 13.564 | 0.20264 | 884 |  | 3.7
85 | Kinectrics 2001 | 25E | "01-2371" | 0.25 | Y | 20 | 7 | CH | 10 | 10 | 610 | 230 | 508 | 508 | 3 | Parallel | 13.202 | 0.20438 | 847 |  | 3.9
97 | Kinectrics 2001 | 25A | "01-2386" | 0.25 | Y | 20 | 7 | CH | 10 | 10 | 610 | 200 | 508 | 508 | 3 | Parallel | 12.73 | 0.21823 | 263.6 |  | 3.6
98 | Kinectrics 2001 | 25A | "01-2387" | 0.25 | Y | 20 | 7 | CH | 10 | 10 | 610 | 200 | 508 | 508 | 3 | Parallel | 11.565 | 0.21996 | 244.8 |  | 3.3
99 | Kinectrics 2001 | 25A | "01-2388" | 0.25 | Y | 20 | 7 | CH | 10 | 10 | 610 | 200 | 508 | 508 | 3 | Parallel | 11.919 | 0.21304 | 255.8 |  | 3.4
103 | Kinectrics 2001 | 19A | "01-2394" | 0.405 | Y | 11.3 | 10 | CH | 25 | 56 | 610 | 193 | 508 | 508 | 3 | Parallel | 4.628 | 0.37411 | 490 |  | 2.8
106 | Kinectrics 2001 | 19A | "01-2398" | 0.405 | Y | 11.3 | 10 | CH | 25 | 56 | 610 | 197 | 508 | 508 | 3 | Parallel | 4.31 | 0.38277 | 458 |  | 2.2
107 | Kinectrics 2001 | 20A | "01-2399" | 0.405 | N | 11.3 | 10 | CH | 25 | 56 | 610 | 196 | 508 | 508 | 3 | Parallel | 5.451 | 0.35506 | 530 |  | 2.4
111 | Kinectrics 2001 | 11A | "01-2405" | 0.59 | Y | 2.7 | 30 | CH | 10 | 10 | 610 | 204 | 508 | 508 | 3 | Parallel | 2.582 | 0.3031 | 215.6 |  | 1.1
112 | Kinectrics 2001 | 11A | "01-2406" | 0.59 | Y | 2.7 | 30 | CH | 10 | 10 | 610 | 199 | 508 | 508 | 3 | Parallel | 2.552 | 0.32388 | 226 |  | 0.9
113 | Kinectrics 2001 | 11A | "01-2407" | 0.59 | Y | 2.7 | 30 | CH | 10 | 10 | 610 | 201 | 508 | 508 | 3 | Parallel | 2.521 | 0.32735 | 229 |  | 0.9
114 | Kinectrics 2001 | 12A | "01-2408" | 0.59 | N | 2.7 | 30 | CH | 40 | 10 | 610 | 201 | 508 | 508 | 3 | Parallel | 2.413 | 0.34813 | 255 |  | 1.1
115 | Kinectrics 2001 | 12A | "01-2411" | 0.59 | N | 2.7 | 30 | CH | 40 | 10 | 610 | 203 | 508 | 508 | 3 | Parallel | 2.391 | 0.35679 | 264 |  | 1.1
116 | Kinectrics 2001 | 12A | "01-2412" | 0.59 | N | 2.7 | 30 | CH | 40 | 10 | 610 | 202 | 508 | 508 | 3 | Parallel | 2.385 | 0.3516 | 261 |  | 0.9
117 | Kinectrics 2001 | 13A | "01-2413" | 0.59 | Y | 2.7 | 30 | CH | 40 | 102 | 610 | 202 | 508 | 508 | 3 | Parallel | 2.244 | 0.38104 | 270 |  | 0.9
118 | Kinectrics 2001 | 13A | "01-2414" | 0.59 | Y | 2.7 | 30 | CH | 40 | 102 | 610 | 407 | 508 | 508 | 3 | Parallel | 2.336 | 0.34467 | 508 |  | 2.2
119 | Kinectrics 2001 | 13A | "01-2415" | 0.59 | Y | 2.7 | 30 | CH | 40 | 102 | 610 | 407 | 508 | 508 | 3 | Parallel | 2.3 | 0.34294 | 502 |  | 1.7
120 | Kinectrics 2001 | 13A | "01-2416" | 0.59 | Y | 2.7 | 30 | CH | 40 | 102 | 610 | 407 | 508 | 508 | 3 | Parallel | 2.382 | 0.33254 | 503 |  | 1.6
121 | Kinectrics 2001 | 14A | "01-2417" | 0.59 | N | 2.7 | 30 | CH | 10 | 102 | 610 | 407 | 508 | 508 | 3 | Parallel | 2.538 | 0.29444 | 426 |  | 1.5
122 | Kinectrics 2001 | 14A | "01-2418" | 0.59 | N | 2.7 | 30 | CH | 10 | 102 | 610 | 407 | 508 | 508 | 3 | Parallel | 2.582 | 0.265 | 416 |  | 1.5
123 | Kinectrics 2001 | 14A | "01-2419" | 0.59 | N | 2.7 | 30 | CH | 10 | 102 | 610 | 407 | 508 | 508 | 3 | Parallel | 2.565 | 0.28232 | 399 |  | 1.2
124 | Kinectrics 2001 | 18A | "01-2422" | 0.59 | Y | 21.4 | 7 | CH | 10 | 102 | 610 | 207 | 508 | 508 | 3 | Parallel | 19.048 | 0.22343 | 1487 |  | 4.5
125 | Kinectrics 2001 | 18A | "01-2423" | 0.59 | Y | 21.4 | 7 | CH | 10 | 102 | 610 | 211 | 508 | 508 | 3 | Parallel | 18.831 | 0.2217 | 1484 |  | 4.2
126 | Kinectrics 2001 | 18A | "01-2424" | 0.59 | Y | 21.4 | 7 | CH | 10 | 102 | 610 | 211 | 508 | 508 | 3 | Parallel | 18.919 | 0.21823 | 1461 |  | 4.3
127 | Kinectrics 2001 | 17A | "01-2425" | 0.59 | N | 21.4 | 7 | CH | 40 | 102 | 610 | 209 | 508 | 508 | 3 | Parallel | 16.459 | 0.33428 | 1869 |  | 5.8
128 | Kinectrics 2001 | 17A | "01-2426" | 0.59 | N | 21.4 | 7 | CH | 40 | 102 | 610 | 209 | 508 | 508 | 3 | Parallel | 16.722 | 0.32562 | 1844 |  | 5.5
129 | Kinectrics 2001 | 17A | "01-2427" | 0.59 | N | 21.4 | 7 | CH | 40 | 102 | 610 | 209 | 508 | 508 | 3 | Parallel | 16.924 | 0.31696 | 1841 |  | 6
130 | Kinectrics 2001 | 16A | "01-2428" | 0.59 | Y | 21.4 | 7 | CH | 40 | 10 | 610 | 212 | 508 | 508 | 3 | Parallel | 17.356 | 0.28751 | 1730 |  | 9.1
131 | Kinectrics 2001 | 16A | "01-2429" | 0.59 | Y | 21.4 | 7 | CH | 40 | 10 | 610 | 208 | 508 | 508 | 3 | Parallel | 17.532 | 0.28751 | 1696 |  | 8.5
132 | Kinectrics 2001 | 16A | "01-2430" | 0.59 | Y | 21.4 | 7 | CH | 40 | 10 | 610 | 208 | 508 | 508 | 3 | Parallel | 17.305 | 0.29098 | 1693 |  | 8.3
133 | Kinectrics 2001 | 15A | "01-2431" | 0.59 | N | 21.4 | 7 | CH | 10 | 10 | 610 | 208 | 508 | 508 | 3 | Parallel | 19.31 | 0.24075 | 1574 |  | 7.7
134 | Kinectrics 2001 | 15A | "01-2432" | 0.59 | N | 21.4 | 7 | CH | 10 | 10 | 610 | 213 | 508 | 508 | 3 | Parallel | 19.071 | 0.23209 | 1597 |  | 8.1
135 | Kinectrics 2001 | 15A | "01-2433" | 0.59 | N | 21.4 | 7 | CH | 10 | 10 | 610 | 213 | 508 | 508 | 3 | Parallel | 18.856 | 0.22516 | 1495 |  | 6.9
136 | Square D 2002 | 28364 | C21 | 0.606 | Y | 22.46 | 5.4648 | CS | 38.1 | 38.1 | 609.6 | 92.2867 | 330.2 | 190.5 | 3 | Parallel | 18.11 | 0.2348 | 637.6 | 1.177 | 1.4958
137 | Square D 2002 | 28365 | C21 | 0.6 | Y | 22.2376 | 5.4648 | CS | 38.1 | 38.1 | 609.6 | 106.4 | 330.2 | 190.5 | 3 | Parallel | 16.0233 | 0.31743 | 901.2 | 2.0473 | 2.3514
138 | Square D 2002 | 28366 | C21 | 0.6 | Y | 22.2376 | 5.4648 | CS | 38.1 | 38.1 | 609.6 | 105.3667 | 330.2 | 190.5 | 3 | Parallel | 15.9933 | 0.31737 | 889.3 | 1.9586 | 2.2714
139 | Square D 2002 | 28367 | D24 | 0.4 | Y | 53.6066 | 5.4648 | CS | 19.05 | 38.1 | 609.6 | 106.6667 | 330.2 | 190.5 | 3 | Parallel | 27.2533 | 0.2779 | 1349 | 2.916 | 3.5965
140 | Square D 2002 | 28368 | D24 | 0.4 | Y | 53.6066 | 5.4648 | CS | 19.05 | 38.1 | 609.6 | 107.0667 | 330.2 | 190.5 | 3 | Parallel | 25.2833 | 0.2842 | 1279.9 | 2.7764 | 3.2648
141 | Square D 2002 | 28369 | D24 | 0.4 | Y | 53.6066 | 5.4648 | CS | 19.05 | 38.1 | 609.6 | 105.0281 | 330.2 | 190.5 | 3 | Parallel | 23.0819 | 0.28399 | 3438.2667 | 2.9289 | 3.3696
142 | Square D 2002 | 28370 | D25 | 0.4 | Y | 53.6066 | 5.4648 | CS | 19.05 | 38.1 | 304.8 | 67.76 | 330.2 | 190.5 | 3 | Parallel | 23.5533 | 0.296 | 784.2 | 5.8303 | 7.412
143 | Square D 2002 | 28371 | D25 | 0.4 | Y | 53.6066 | 5.4648 | CS | 19.05 | 38.1 | 304.8 | 67.02 | 330.2 | 190.5 | 3 | Parallel | 24.92 | 0.2885 | 806.3 | 5.3402 | 7.2697
144 | Square D 2002 | 28372 | D25 | 0.4 | Y | 53.6066 | 5.4648 | CS | 19.05 | 38.1 | 304.8 | 67.12 | 330.2 | 190.5 | 3 | Parallel | 26.5433 | 0.27653 | 818.2 | 5.9402 | 8.2119
145 | Square D 2002 | 28373 | D26 | 0.4 | Y | 53.6066 | 5.4648 | CS | 19.05 | 38.1 | 1828.8 | 107.0333 | 330.2 | 190.5 | 3 | Parallel | 24.3433 | 0.2941 | 1282.8 | 0.27937 | 0.32734
146 | Square D 2002 | 28374 | D26A | 0.4 | Y | 53.6066 | 5.4648 | CS | 19.05 | 38.1 | 1828.8 | 539.4667 | 330.2 | 190.5 | 3 | Parallel | 27.2033 | 0.28153 | 6922 | 4.998 | 5.7126
147 | Square D 2002 | 28392 | D26B | 0.4 | Y | 53.6066 | 5.4648 | CS | 19.05 | 38.1 | 1828.8 | 180.2 | 330.2 | 190.5 | 3 | Parallel | 25.6467 | 0.28407 | 2171.8 | 0.92805 | 1.1323
148 | Square D 2002 | 28445 | D26B | 0.4 | Y | 53.6066 | 5.4648 | CS | 19.05 | 38.1 | 1828.8 | 177.8 | 330.2 | 190.5 | 3 | Parallel | 29.7933 | 0.25973 | 2283 | 0.61329 | 0.7425
149 | Square D 2002 | 28446 | D26B | 0.4 | Y | 53.6066 | 5.4648 | CS | 19.05 | 38.1 | 1828.8 | 174.7333 | 330.2 | 190.5 | 3 | Parallel | 28.3267 | 0.26883 | 2186.2 | 0.54939 | 0.74073
150 | Square D 2002 | 28382 | F28 | 0.4 | HRG | 53.6066 | 5.4648 | CS | 19.05 | 38.1 | 609.6 | 110.6 | 330.2 | 190.5 | 3 | Parallel | 28.0433 | 0.2789 | 1404 | 3.2122 | 3.9651
151 | Square D 2002 | 28383 | F28 | 0.4 | HRG | 53.6066 | 5.4648 | CS | 19.05 | 38.1 | 609.6 | 110.6 | 330.2 | 190.5 | 3 | Parallel | 25.6667 | 0.28917 | 1347.4 | 2.8787 | 3.4641
152 | Square D 2002 | 28384 | F28 | 0.4 | HRG | 53.6066 | 5.4648 | CS | 19.05 | 38.1 | 609.6 | 111.8333 | 330.2 | 190.5 | 3 | Parallel | 26.36 | 0.28117 | 1331.9 | 0.41263 | 0.50184
153 | Square D 2002 | 28385 | F29 | 0.485 | HRG | 52.56 | 5.4648 | CS | 19.05 | 38.1 | 609.6 | 108.0667 | 330.2 | 190.5 | 3 | Parallel | 31 | 0.30553 | 1726.2 | 3.8293 | 4.3706
154 | Square D 2002 | 28386 | F29 | 0.485 | HRG | 52.56 | 5.4648 | CS | 19.05 | 38.1 | 609.6 | 106.3 | 330.2 | 190.5 | 3 | Parallel | 30.87 | 0.31257 | 1732.6 | 4.2364 | 4.8071
155 | Square D 2002 | 28387 | F29 | 0.485 | HRG | 52.56 | 5.4648 | CS | 19.05 | 38.1 | 609.6 | 105.5333 | 330.2 | 190.5 | 3 | Parallel | 31.03 | 0.3097 | 1706.7 | 3.8794 | 4.3717
156 | Square D 2002 | 28389 | E27 | 0.4 | Y | 54.1856 | 5.7967 | CS | 19.05 | 38.1 | 609.6 | 103.2667 | 330.2 | 190.5 | 3 | Parallel | 25.7733 | 0.28623 | 1257.8 | 2.6512 | 3.0823
157 | Square D 2002 | 28390 | E27 | 0.4 | Y | 54.1856 | 5.7967 | CS | 19.05 | 38.1 | 609.6 | 102.5 | 330.2 | 190.5 | 3 | Parallel | 25.2867 | 0.28917 | 1235.8 | 2.6577 | 3.1813
158 | Square D 2002 | 28391 | E27 | 0.4 | Y | 54.1856 | 5.7967 | CS | 19.05 | 38.1 | 609.6 | 108.0667 | 330.2 | 190.5 | 3 | Parallel | 24.99 | 0.28653 | 1247.9
159 | Square D 2002 | 28393 | BC19 | 0.4 | Y | 53.6066 | 5.4648 | CS | 31.75 | 38.1 | 609.6 | 107.2333 | 330.2 | 190.5 | 3 | Parallel | 24.3367 | 0.297 | 1286.9 | 2.3922 | 3.0364
160 | Square D 2002 | 28394 | BC19 | 0.4 | Y | 53.6066 | 5.4648 | CS | 31.75 | 38.1 | 609.6 | 109.1 | 330.2 | 190.5 | 3 | Parallel | 22.1367 | 0.30617 | 1213.2 | 2.5152 | 3.084
161 | Square D 2002 | 28395 | BC19 | 0.4 | Y | 53.6066 | 5.4648 | CS | 31.75 | 38.1 | 609.6 | 104.1333 | 330.2 | 190.5 | 3 | Parallel | 20.68 | 0.31797 | 1130.5 | 2.3584 | 2.8183
162 | Square D 2002 | 28396 | B14 | 0.4 | Y | 103.3402 | 5.4648 | CS | 31.75 | 38.1 | 609.6 | 61.3533 | 330.2 | 190.5 | 3 | Parallel | 26.8533 | 0.34203 | 943.1 | 2.0213 | 2.4143
163 | Square D 2002 | 28397 | B14 | 0.4 | Y | 103.3402 | 5.4648 | CS | 31.75 | 38.1 | 609.6 | 60.64 | 330.2 | 190.5 | 3 | Parallel | 27.2967 | 0.33997 | 941.5 | 1.9484 | 2.3088
164 | Square D 2002 | 28398 | B14 | 0.4 | Y | 103.3402 | 5.4648 | CS | 31.75 | 38.1 | 609.6 | 59.8267 | 330.2 | 190.5 | 3 | Parallel | 28.66 | 0.33477 | 964.2 | 2.0357 | 2.4203
165 | Square D 2002 | 28399 | B15 | 0.6 | Y | 100.5941 | 5.1673 | CS | 31.75 | 38.1 | 609.6 | 62.58 | 330.2 | 190.5 | 3 | Parallel | 54.4167 | 0.37287 | 2124 | 5.8531 | 7.6384
166 | Square D 2002 | 28400 | B15 | 0.6 | Y | 100.5941 | 5.1673 | CS | 31.75 | 38.1 | 609.6 | 63.0533 | 330.2 | 190.5 | 3 | Parallel | 52.23 | 0.3893 | 2078.9 | 5.8561 | 7.6515
167 | Square D 2002 | 28404 | A3 | 0.208 | Y | 87.5 | 6.1695 | CS | 12.7 | 38.1 | 609.6 | 71.6267 | 330.2 | 190.5 | 3 | Parallel | 20.8533 | 0.187 | 430.6 | 0.80351 | 1.1199
171 | Square D 2002 | 28408 | B13 | 0.4 | Y | 103.3402 | 5.4648 | CS | 12.7 | 38.1 | 609.6 | 64.68 | 330.2 | 190.5 | 3 | Parallel | 35.9 | 0.31303 | 1193.7 | 2.5234 | 2.8307
172 | Square D 2002 | 28409 | B13 | 0.4 | Y | 103.3402 | 5.4648 | CS | 12.7 | 38.1 | 609.6 | 61.23 | 330.2 | 190.5 | 3 | Parallel | 44.57 | 0.2849 | 1300 | 3.1827 | 3.6666
173 | Square D 2002 | 27244 | B12 | 0.405 | Y | 2.5511 | 1.878 | CS | 31.75 | 38.1 | 609.6 | 92.1667 | 330.2 | 190.5 | 3 | Parallel | 2.1223 | 0.1753 | 19.582 | 0.038158 | 0.053367
174 | Square D 2002 | 27245 | B12 | 0.405 | Y | 2.5511 | 1.878 | CS | 31.75 | 38.1 | 609.6 | 31.1667 | 330.2 | 190.5 | 3 | Parallel | 1.549 | 0.25783 | 15.534 | 0.037399 | 0.046539
175 | Square D 2002 | 27256 | B16 | 0.61 | N | 2.8433 | 1.9303 | CS | 31.75 | 38.1 | 609.6 | 344.7 | 330.2 | 190.5 | 3 | Parallel | 2.058 | 0.26637 | 306.68 | 0.55854 | 0.67833
176 | Square D 2002 | 27258 | B16 | 0.611 | N | 2.848 | 1.9303 | CS | 31.75 | 38.1 | 609.6 | 807.5 | 330.2 | 190.5 | 3 | Parallel | 2.05 | 0.27607 | 745.3 | 1.9683 | 2.6649
177 | Square D 2002 | 27259 | B16 | 0.611 | N | 2.848 | 1.9303 | CS | 31.75 | 38.1 | 609.6 | 606.6667 | 330.2 | 190.5 | 3 | Parallel | 2.031 | 0.2822 | 564.6 | 1.7352 | 2.4557
178 | Square D 2002 | 27261 | B16A | 0.603 | N | 3.063 | 0.77608 | CS | 31.75 | 38.1 | 609.6 | 525.6667 | 330.2 | 190.5 | 3 | Parallel | 1.9013 | 0.29103 | 470.2 | 1.4542 | 1.9893
179 | Square D 2002 | 27262 | B16A | 0.603 | N | 3.063 | 0.77608 | CS | 31.75 | 38.1 | 609.6 | 526.3333 | 330.2 | 190.5 | 3 | Parallel | 1.8943 | 0.29453 | 474.7 | 1.6255 | 2.2974
180 | Square D 2002 | 27263 | B16A | 0.603 | N | 3.063 | 0.77608 | CS | 31.75 | 38.1 | 609.6 | 526 | 330.2 | 190.5 | 3 | Parallel | 1.8887 | 0.2946 | 458.1 | 1.5774 | 2.1392
181 | Square D 2002 | 27266 | BC17 | 0.606 | Y | 2.8247 | 1.9303 | CS | 19.05 | 38.1 | 609.6 | 529.6667 | 330.2 | 190.5 | 3 | Parallel | 2.063 | 0.27137 | 443.3 | 1.3829 | 1.8565
182 | Square D 2002 | 27267 | BC17 | 0.606 | Y | 2.8247 | 1.9303 | CS | 19.05 | 38.1 | 609.6 | 528 | 330.2 | 190.5 | 3 | Parallel | 2.0507 | 0.27633 | 450.8 | 1.362 | 1.8237
183 | Square D 2002 | 27268 | BC17 | 0.606 | Y | 2.8247 | 1.9303 | CS | 19.05 | 38.1 | 609.6 | 530.3333 | 330.2 | 190.5 | 3 | Parallel | 2.0437 | 0.27747 | 459.4 | 1.406 | 1.6876
188 | Square D 2002 | 27281 | AcB11 | 0.405 | Y | 2.5511 | 0.56673 | CS | 7.112 | 9.144 | 609.6 | 531.1667 | 330.2 | 190.5 | 3 | Parallel | 1.8863 | 0.17943 | 242.44 | 0.5913 | 0.70799
189 | Square D 2002 | 27283 | AcB11 | 0.405 | Y | 2.5511 | 0.56673 | CS | 7.112 | 9.144 | 609.6 | 527.6667 | 330.2 | 190.5 | 3 | Parallel | 1.8353 | 0.18727 | 243.71 | 0.56353 | 0.77574
190 | Square D 2002 | 27284 | AcB11 | 0.405 | Y | 2.5511 | 0.56673 | CS | 7.112 | 9.144 | 609.6 | 530.5 | 330.2 | 190.5 | 3 | Parallel | 1.8987 | 0.1967 | 244.56 | 0.64602 | 0.93996
193 | Square D 2002 | 27290 | AB6 | 0.609 | Y | 2.8588 | 1.9845 | CS | 7.112 | 9.144 | 304.8 | 534.5 | 330.2 | 190.5 | 3 | Parallel | 2.189 | 0.25993 | 431.4 | 1.7657 | 2.6202
194 | Square D 2002 | 27291 | AB6 | 0.609 | Y | 2.8588 | 1.9845 | CS | 7.112 | 9.144 | 304.8 | 536.3333 | 330.2 | 190.5 | 3 | Parallel | 2.2157 | 0.25317 | 418.2 | 1.5881 | 2.1564
195 | Square D 2002 | 27292 | AB6 | 0.609 | Y | 2.8588 | 1.9845 | CS | 7.112 | 9.144 | 304.8 | 530.6667 | 330.2 | 190.5 | 3 | Parallel | 2.1957 | 0.26183 | 419.5 | 1.6625 | 2.2266
196 | Square D 2002 | 28448 | B13 | 0.4 | Y | 103.3402 | 5.4648 | CS | 7.112 | 38.1 | 609.6 | 69.92 | 330.2 | 190.5 | 3 | Parallel | 50.5067 | 0.25927 | 1480.5 | 4.1185 | 4.833
197 | Square D 2002 | 28449 | B13 | 0.4 | Y | 103.3402 | 5.4648 | CS | 7.112 | 38.1 | 609.6 | 68.88 | 330.2 | 190.5 | 3 | Parallel | 45.9767 | 0.27583 | 1399.8 | 3.5941 | 4.4685
198 | Square D 2002 | 28450 | B13 | 0.4 | Y | 103.3402 | 5.4648 | CS | 7.112 | 38.1 | 609.6 | 69.1333 | 330.2 | 190.5 | 3 | Parallel | 48.3767 | 0.2649 | 1389.1 | 4.0709 | 4.9815
199 | Square D 2002 | 28451 | AB7 | 0.606 | Y | 101.6 | 5.1673 | CS | 7.112 | 38.1 | 609.6 | 43.36 | 330.2 | 190.5 | 3 | Parallel | 65.16 | 0.29297 | 1375.5 | 4.295 | 4.7988
200 | KEMA 2001 | 450 v tests | 169 | 0.45 | N | 79.6 | 10.75 | CH | 38.1 | 10000 | 610 | 216.4 | 10000 | 10000 | 3 | Parallel | 19 | 0.236 | 4066 | 7.6603 | 10.6245
201 | KEMA 2001 | 450 v tests | 170 | 0.45 | N | 79.6 | 10.75 | CH | 38.1 | 10000 | 610 | 216.8 | 10000 | 10000 | 3 | Parallel | 26.7 | 0.235 | 4446 | 8.4915 | 11.9205
202 | KEMA 2001 | 450 v tests | 171 | 0.45 | N | 79.6 | 10.75 | CH | 38.1 | 10000 | 610 | 217 | 10000 | 10000 | 3 | Parallel | 20.1 | 0.233 | 4580 | 8.8811 | 12.3255
203 | Kinectrics 2400 | 1640 | OPEN - 3 PHASE | 2.3815 | N | 2.5767 |  | CH | 102 | 152 | 609.6 | 204.2 | 953 | 762 | 3 | Parallel | 2.5233 | 0.66289 | * | 0.65957 | 0.7695
204 | Kinectrics 2400 | 1641 | OPEN - 3 PHASE | 2.3815 | N | 2.5767 |  | CH | 102 | 152 | 609.6 | 198.9 | 953 | 762 | 3 | Parallel | 2.5567 | 0.58137 | 459.1 | 0.52843 | 0.621
205 | Kinectrics 2400 | 1642 | OPEN - 3 PHASE | 2.3815 | N | 2.5767 |  | CH | 102 | 152 | 609.6 | 203.1 | 953 | 762 | 3 | Parallel | 2.5667 | 0.55239 | 453 | 0.56893 | 0.6615
206 | Kinectrics 2400 | 1643 | OPEN - 3 PHASE | 2.3815 | N | 2.5767 |  | CH | 102 | 152 | 609.6 | 201.7 | 953 | 762 | 3 | Parallel | 2.5767 | 0.59771 | * | 0.54193 | 0.621
207 | Kinectrics 2400 | 1645 | OPEN - 3 PHASE | 2.3798 | N | 4.8733 |  | CH | 102 | 152 | 609.6 | 197.5 | 953 | 762 | 3 | Parallel | 4.8067 | 0.66116 | * | 1.1186 | 1.215
208 | Kinectrics 2400 | 1646 | OPEN - 3 PHASE | 2.378 | N | 4.8733 |  | CH | 102 | 152 | 609.6 | 194.2 | 953 | 762 | 3 | Parallel | 4.8033 | 0.66382 | * | 1.0029 | 1.107
209 | Kinectrics 2400 | 1647 | OPEN - 3 PHASE | 2.3763 | N | 4.8733 |  | CH | 102 | 152 | 609.6 | 192.4 | 953 | 762 | 3 | Parallel | 4.88 | 0.68431 | 963.15 | 1.1494 | 1.215
210 | Kinectrics 2400 | 1648 | OPEN - 3 PHASE | 2.3728 | N | 4.8733 |  | CH | 102 | 152 | 609.6 | 189.7 | 953 | 762 | 3 | Parallel | 4.7533 | 0.71012 | 985.84 | 1.0954 | 1.188
211 | Kinectrics 2400 | 1650 | OPEN - 3 PHASE | 2.3763 | N | 6.9533 |  | CH | 102 | 152 | 609.6 | 196.6 | 953 | 762 | 3 | Parallel | 6.7367 | 0.69124 | 1446.61 | 1.6489 | 1.782
212 | Kinectrics 2400 | 1651 | OPEN - 3 PHASE | 2.3728 | N | 6.9533 |  | CH | 102 | 152 | 609.6 | 193.8 | 953 | 762 | 3 | Parallel | 6.7133 | 0.70556 | 1438.87 | 1.62 | 1.7415
213 | Kinectrics 2400 | 1652 | OPEN - 3 PHASE | 2.3728 | N | 6.9533 |  | CH | 102 | 152 | 609.6 | 196.6 | 953 | 762 | 3 | Parallel | 6.7767 | 0.73801 | 1547.66 | 1.7319 | 1.89
214 | Kinectrics 2400 | 1653 | OPEN - 3 PHASE | 2.3728 | N | 6.9533 |  | CH | 102 | 152 | 609.6 | 195.2 | 953 | 762 | 3 | Parallel | 6.7967 | 0.72871 | 1507.38 | 1.7589 | 1.863
215 | Kinectrics 2400 | 1656 | OPEN - 3 PHASE | 2.378 | N | 11.6367 |  | CH | 102 | 152 | 609.6 | 191 | 953 | 762 | 3 | Parallel | 11.1067 | 0.71024 | 2443.86 | 2.7791 | 3.0375
216 | Kinectrics 2400 | 1657 | OPEN - 3 PHASE | 2.3711 | N | 11.6367 |  | CH | 102 | 152 | 609.6 | 186.7 | 953 | 762 | 3 | Parallel | 11.1667 | 0.70019 | 2330.73 | 2.6402 | 2.9295
217 | Kinectrics 2400 | 1658 | OPEN - 3 PHASE | 2.3676 | N | 11.6367 |  | CH | 102 | 152 | 609.6 | 194.2 | 953 | 762 | 3 | Parallel | 10.9933 | 0.7421 | 2497.65 | 2.6884 | 2.9835
218 | Kinectrics 2400 | 1659 | OPEN - 3 PHASE | 2.3711 | N | 11.6367 |  | CH | 102 | 152 | 609.6 | 199.8 | 953 | 762 | 3 | Parallel | 11.01 | 0.77842 | 2719.46 | 2.9526 | 3.2535
219 | Kinectrics 2400 | 1660 | OPEN - 2 PHASE (A-B) | 2.3694 | N | 5.5833 |  | CH | 102 | 152 | 609.6 | 198.4 | 953 | 762 | 3 | Parallel | 5.5833 | * | * | 1.6451 | 1.89
220 | Kinectrics 2400 | 1661 | OPEN - 2 PHASE (A-B) | 2.3694 | N | 5.5833 |  | CH | 102 | 152 | 609.6 | 198 | 953 | 762 | 3 | Parallel | 5.34 | * | * | 1.6836 | 1.836
221 | Kinectrics 2400 | 1662 | OPEN - 2 PHASE (A-B) | 2.3711 | N | 5.5833 |  | CH | 102 | 152 | 609.6 | 198.9 | 953 | 762 | 3 | Parallel | 5.89 | * | * | 1.5081 | 1.7955
222 | Kinectrics 2400 | 1663 | OPEN - 2 PHASE (A-B) | 2.378 | N | 5.5833 |  | CH | 102 | 152 | 609.6 | 196.1 | 953 | 762 | 3 | Parallel | 5.6267 | * | * | 1.4541 | 1.6065
223 | Kinectrics 2400 | 1666 | OPEN - 3 PHASE | 2.3746 | N | 14.5167 |  | CH | 102 | 152 | 609.6 | 207.3 | 953 | 762 | 3 | Parallel | 13.7 | 0.79158 | 3629.29 | 4.2891 | 4.5225
224 | Kinectrics 2400 | 1667 | OPEN - 3 PHASE | 2.3815 | N | 14.5167 |  | CH | 102 | 152 | 609.6 | 207.8 | 953 | 762 | 3 | Parallel | 13.72 | 0.73604 | 3387.88 | 3.5293 | 3.9285
225 | Kinectrics 2400 | 1668 | OPEN - 3 PHASE | 2.378 | N | 14.5167 |  | CH | 102 | 152 | 609.6 | 214.4 | 953 | 762 | 3 | Parallel | 13.6733 | 0.71607 | 3359 | 3.6759 | 4.0365
226 | Kinectrics 2400 | 1669 | OPEN - 3 PHASE | 2.3798 | N | 14.5167 |  | CH | 102 | 152 | 609.6 | 202.7 | 953 | 762 | 3 | Parallel | 13.7333 | 0.70111 | 3194.79 | 3.4579 | 3.6315
227 | Kinectrics 2400 | 1672 | OPEN - 3 PHASE | 2.3399 | N | 16.21 |  | CH | 102 | 152 | 609.6 | 212 | 953 | 762 | 3 | Parallel | 15.3033 | 0.78546 | 4131.96 | 4.7308 | 5.049
228 | Kinectrics 2400 | 1673 | OPEN - 3 PHASE | 2.3382 | N | 16.21 |  | CH | 102 | 152 | 609.6 | 211.5 | 953 | 762 | 3 | Parallel | 15.1433 | 0.78639 | 4087.42 | 4.2004 | 4.617
229 | Kinectrics 2400 | 1674 | OPEN - 3 PHASE | 2.3382 | N | 16.21 |  | CH | 102 | 152 | 609.6 | 208.7 | 953 | 762 | 3 | Parallel | 15.2267 | 0.76069 | 3881.61 | 4.5996 | 5.0355
230 | Kinectrics 2400 | 1675 | OPEN - 3 PHASE | 2.3347 | N | 16.21 |  | CH | 102 | 152 | 609.6 | 211.5 | 953 | 762 | 3 | Parallel | 15.1667 | 0.72767 | 3775.25 | 4.4724 | 4.8195
231 | Kinectrics 2400 | 1677 | BOX - 3 PH - 45"X30"X30" | 2.3694 | N | 11.6367 |  | CH | 102 | 152 | 609.6 | 210.6 | 953 | 762 | 3 | Parallel | 11.0933 | 0.59933 | 2269.85 | 3.942 | 4.9545
232 | Kinectrics 2400 | 1678 | BOX - 3 PH - 45"X30"X30" | 2.3728 | N | 11.6367 |  | CH | 102 | 152 | 609.6 | 211.1 | 953 | 762 | 3 | Parallel | 11.02 | 0.60966 | 2329.8 | 3.6681 | 5.1435
233 | Kinectrics 2400 | 1679 | BOX - 3 PH - 45"X30"X30" | 2.3798 | N | 11.6367 |  | CH | 102 | 152 | 609.6 | 206.9 | 953 | 762 | 3 | Parallel | 11.1967 | 0.59858 | 2236.47 | 3.6604 | 5.2785
234 | Kinectrics 2400 | 1680 | BOX - 3 PH - 45"X30"X30" | 2.3728 | N | 11.6367 |  | CH | 102 | 152 | 609.6 | 208.3 | 953 | 762 | 3 | Parallel | 11.1333 | 0.57993 | 2186.96 | 3.3229 | 4.185
235 | Kinectrics 2400 | 1682 | BOX - 3 PH - 45"X30"X30" | 2.3313 | N | 6.81 |  | CH | 102 | 152 | 609.6 | 210.1 | 953 | 762 | 3 | Parallel | 6.5133 | 0.59067 | 1310.85 | 2.5766 | 3.4695
236 | Kinectrics 2400 | 1683 | BOX - 3 PH - 45"X30"X30" | 2.333 | N | 6.81 |  | CH | 102 | 152 | 609.6 | 200.8 | 953 | 762 | 3 | Parallel | 6.6233 | 0.60891 | 1322.88 | 2.673 | 3.537
237 | Kinectrics 2400 | 1684 | BOX - 3 PH - 45"X30"X30" | 2.3278 | N | 6.81 |  | CH | 102 | 152 | 609.6 | 206.9 | 953 | 762 | 3 | Parallel | 6.57 | 0.6133 | 1348.23 | 2.7019 | 3.348
238 | Kinectrics 2400 | 1685 | BOX - 3 PH - 45"X30"X30" | 2.3365 | N | 6.81 |  | CH | 102 | 152 | 609.6 | 220 | 953 | 762 | 3 | Parallel | 6.5933 | 0.61041 | 1416.76 | 2.9546 | 3.834
239 | Kinectrics 2400 | 1687 | BOX - 3 PH - 45"X30"X30" | 2.3347 | N | 4.7867 |  | CH | 102 | 152 | 609.6 | 210.6 | 953 | 762 | 3 | Parallel | 4.7 | 0.59044 | 932.41 | 2.0211 | 2.6865
240 | Kinectrics 2400 | 1688 | BOX - 3 PH - 45"X30"X30" | 2.3347 | N | 4.7867 |  | CH | 102 | 152 | 609.6 | 211.5 | 953 | 762 | 3 | Parallel | 4.6967 | 0.59633 | 941.96 | 2.1291 | 2.808
241 | Kinectrics 2400 | 1689 | BOX - 3 PH - 45"X30"X30" | 2.333 | N | 4.7867 |  | CH | 102 | 152 | 609.6 | 214.8 | 953 | 762 | 3 | Parallel | 4.69 | 0.58755 | 942.5 | 2.1446 | 2.6595
242 | Kinectrics 2400 | 1690 | BOX - 3 PH - 45"X30"X30" | 2.3365 | N | 4.7867 |  | CH | 102 | 152 | 609.6 | 212.9 | 953 | 762 | 3 | Parallel | 4.7 | 0.61007 | 982.37 | 2.1195 | 2.808
243 | Kinectrics 2400 | 1692 | BOX - 3 PH - 45"X30"X30" | 2.3365 | N | 2.5267 |  | CH | 102 | 152 | 609.6 | 212 | 953 | 762 | 3 | Parallel | 2.5267 | 0.54639 | 453.19 | 1.1282 | 1.35
244 | Kinectrics 2400 | 1693 | BOX - 3 PH - 45"X30"X30" | 2.3382 | N | 2.5267 |  | CH | 102 | 152 | 609.6 | 203.6 | 953 | 762 | 3 | Parallel | 2.4867 | 0.51106 | 422.19 | 0.95657 | 1.161
245 | Kinectrics 2400 | 1694 | BOX - 3 PH - 45"X30"X30" | 2.3399 | N | 2.5267 |  | CH | 102 | 152 | 609.6 | 209.2 | 953 | 762 | 3 | Parallel | 2.4933 | 0.536 | 436.1 | 1.0684 | 1.4175
246 | Kinectrics 2400 | 1695 | BOX - 3 PH - 45"X30"X30" | 2.3659 | N | 2.5267 |  | CH | 102 | 152 | 609.6 | 197 | 953 | 762 | 3 | Parallel | 2.54 | 0.51082 | 409.98 | 1.2266 | 1.458
247 | Kinectrics 2400 | 1698 | BOX - 3 PH - 45"X30"X30" | 2.3607 | N | 16.4033 |  | CH | 102 | 152 | 609.6 | 207.3 | 953 | 762 | 3 | Parallel | 15.5167 | 0.58467 | 3016.43 | 4.428 | 5.778
248 | Kinectrics 2400 | 1699 | BOX - 3 PH - 45"X30"X30" | 2.3573 | N | 16.4033 |  | CH | 102 | 152 | 609.6 | 205 | 953 | 762 | 3 | Parallel | 15.64 | 0.5898 | 3021.01 | 4.5553 | 5.3595
249 | Kinectrics 2400 | 1700 | BOX - 3 PH - 45"X30"X30" | 2.3624 | N | 16.4033 |  | CH | 102 | 152 | 609.6 | 206.4 | 953 | 762 | 3 | Parallel | 15.58 | 0.61804 | 3284.5 | 4.3952 | 5.6565
250 | Kinectrics 2400 | 1701 | BOX - 3 PH - 45"X30"X30" | 2.359 | N | 16.4033 |  | CH | 102 | 152 | 609.6 | 212 | 953 | 762 | 3 | Parallel | 15.4167 | 0.63836 | 3418.96 | 4.4743 | 6.0615
251 | Kinectrics 2400 | 1703 | BOX - 3 PH - 45"X30"X30" | 2.3694 | N | 14.4 |  | CH | 102 | 152 | 609.6 | 218.6 | 953 | 762 | 3 | Parallel | 13.7267 | 0.54506 | 2571.56 | 5.9342 | 6.669
252 | Kinectrics 2400 | 1704 | BOX - 3 PH - 45"X30"X30" | 2.3711 | N | 14.4 |  | CH | 102 | 152 | 609.6 | 212.9 | 953 | 762 | 3 | Parallel | 13.7667 | 0.58495 | 2729.07 | 5.3479 | 6.0885
253 | Kinectrics 2400 | 1705 | BOX - 3 PH - 45"X30"X30" | 2.3694 | N | 14.4 |  | CH | 102 | 152 | 609.6 | 211.1 | 953 | 762 | 3 | Parallel | 13.6 | 0.60891 | 2876.41 | 4.4936 | 6.291
254 | Kinectrics 2400 | 1706 | BOX - 3 PH - 45"X30"X30" | 2.3676 | N | 14.4 |  | CH | 102 | 152 | 609.6 | 215.3 | 953 | 762 | 3 | Parallel | 13.7 | 0.6006 | 2898.21 | 3.9786 | 5.454
255 | Kinectrics 2400 | 1707 | BOX - 2 PH(A-B) - 45"X30"X30" | 2.3694 | N | 13 |  | CH | 102 | 152 | 609.6 | 200.8 | 953 | 762 | 2 | Parallel | 7.76 |  | * | 3.3596 | 4.4955
256 | Kinectrics 2400 | 1708 | BOX - 2 PH(A-B) - 45"X30"X30" | 2.3694 | N | 13 |  | CH | 102 | 152 | 609.6 | 198.4 | 953 | 762 | 2 | Parallel | 7.68 |  | * | 3.078 | 3.834
257 | Kinectrics 2400 | 1709 | BOX - 2 PH(A-B) - 45"X30"X30" | 2.3676 | N | 13 |  | CH | 102 | 152 | 609.6 | 206.9 | 953 | 762 | 2 | Parallel | 7.7533 |  | * | 3.5756 | 4.4415
258 | Kinectrics 2400 | 1710 | BOX - 2 PH(A-B) - 45"X30"X30" | 2.3694 | N | 13 |  | CH | 102 | 152 | 609.6 | 200.3 | 953 | 762 | 2 | Parallel | 7.8733 |  | * | 3.4946 | 4.455
259 | Kinectrics 2400 | 1711 | BOX - 3 PH - 45"X30"X30" | 2.3521 | N | 15 |  | CH | 102 | 152 | 762 | 209.7 | 953 | 762 | 3 | Parallel | 13.5033 | 0.61197 | 2796.05 | 3.1455 | 4.5225
260 | Kinectrics 2400 | 1712 | BOX - 3 PH - 45"X30"X30" | 2.3573 | N | 15 |  | CH | 102 | 152 | 762 | 204.5 | 953 | 762 | 3 | Parallel | 13.56 | 0.62791 | 2841.13 | 3.4444 | 4.887
261 | Kinectrics 2400 | 1713 | BOX - 3 PH - 45"X30"X30" | 2.3503 | N | 15 |  | CH | 102 | 152 | 762 | 201.2 | 953 | 762 | 3 | Parallel | 13.55 | 0.63922 | 2836.6 | 3.3538 | 4.5225
262 | Kinectrics 2400 | 1714 | BOX - 3 PH - 45"X30"X30" | 2.3521 | N | 15 |  | CH | 102 | 152 | 762 | 206.4 | 953 | 762 | 3 | Parallel | 13.6033 | 0.64275 | 2981.16 | 3.3075 | 4.7655
263 | Kinectrics 2400 | 1715 | BOX - 3 PH - 45"X30"X30" | 2.3486 | N | 15 |  | CH | 102 | 152 | 914.4 | 206.4 | 953 | 762 | 3 | Parallel | 13.4167 | 0.64332 | 2906.24 | 2.8311 | 3.996
264 | Kinectrics 2400 | 1716 | BOX - 3 PH - 45"X30"X30" | 2.3434 | N | 15 |  | CH | 102 | 152 | 914.4 | 206.4 | 953 | 762 | 3 | Parallel | 13.5267 | 0.61757 | 2843.38 | 2.9411 | 4.0905
265 | Kinectrics 2400 | 1717 | BOX - 3 PH - 45"X30"X30" | 2.3434 | N | 15 |  | CH | 102 | 152 | 914.4 | 212.9 | 953 | 762 | 3 | Parallel | 13.56 | 0.61619 | 2942.83 | 2.808 | 3.9285
266 | Kinectrics 2400 | 1718 | BOX - 3 PH - 45"X30"X30" | 2.3417 | N | 15 |  | CH | 102 | 152 | 914.4 | 207.8 | 953 | 762 | 3 | Parallel | 13.3967 | 0.62583 | 2847.16 | 2.5611 | 3.861
267 | Kinectrics 2400 | 1720 | BOX - 3 PH - 45"X30"X30" | 2.3347 | N | 15 |  | CH | 102 | 152 | 1219.2 | 204.5 | 953 | 762 | 3 | Parallel | 13.66 | 0.59171 | 2667.26 | 1.9421 | 2.754
268 | Kinectrics 2400 | 1721 | BOX - 3 PH - 45"X30"X30" | 2.3347 | N | 15 |  | CH | 102 | 152 | 1219.2 | 209.7 | 953 | 762 | 3 | Parallel | 13.4633 | 0.60914 | 2814.37 | 2.1754 | 3.0915
269 | Kinectrics 2400 | 1722 | BOX - 3 PH - 45"X30"X30" | 2.3347 | N | 15 |  | CH | 102 | 152 | 1219.2 | 231.7 | 953 | 762 | 3 | Parallel | 13.3533 | 0.65533 | 3297.73 | 2.4907 | 3.726
270 | Kinectrics 2400 | 1725 | BOX - 3 PH - 45"X30"X30" | 2.3382 | N | 15 |  | CH | 102 | 152 | 1219.2 | 227.5 | 953 | 762 | 3 | Parallel | 13.4867 | 0.60031 | 2984.04 | 2.0867 | 2.9295
271 | Kinectrics 2400 | 1726 | BOX - 3 PH - 45"X30"X30" | 2.3382 | N | 15 |  | CH | 102 | 152 | 1524 | 228.9 | 953 | 762 | 3 | Parallel | 13.5067 | 0.6088 | 3069.87 | 1.8534 | 2.9565
272 | Kinectrics 2400 | 1727 | BOX - 3 PH - 45"X30"X30" | 2.3399 | N | 15 |  | CH | 102 | 152 | 1524 | 221.8 | 953 | 762 | 3 | Parallel | 13.5767 | 0.5969 | 2924.56 | 1.7936 | 2.565
273 | Kinectrics 2400 | 1728 | BOX - 3 PH - 45"X30"X30" | 2.3365 | N | 15 |  | CH | 102 | 152 | 1524 | 236.1 | 953 | 762 | 3 | Parallel | 13.5933 | 0.59921 | 3123.69 | 1.8861 | 2.4705
274 | Kinectrics 2400 | 1729 | BOX - 3 PH - 45"X30"X30" | 2.3382 | N | 15 |  | CH | 102 | 152 | 1524 | 181.8 | 953 | 762 | 3 | Parallel | 13.4867 | 0.60828 | 2443.86 | 1.5544 | 2.214
275 | Kinectrics 2400 | 1730 | BOX - 3 PH - 45"X30"X30" | 2.3451 | N | 15 |  | CH | 102 | 152 | 457.2 | 185.6 | 953 | 762 | 3 | Parallel | 13.48 | 0.58386 | 2408.03 | 4.4608 | 5.6835
276 | Kinectrics 2400 | 1731 | BOX - 3 PH - 45"X30"X30" | 2.3434 | N | 15 |  | CH | 102 | 152 | 457.2 | 193.8 | 953 | 762 | 3 | Parallel | 13.5967 | 0.59125 | 2550.31 | 4.5013 | 5.4675
277 | Kinectrics 2400 | 1732 | BOX - 3 PH - 45"X30"X30" | 2.3486 | N | 15 |  | CH | 102 | 152 | 457.2 | 193.8 | 953 | 762 | 3 | Parallel | 13.7133 | 0.57445 | 2446.39 | 4.3451 | 5.9265
278 | Kinectrics 2400 | 1733 | BOX - 3 PH - 45"X30"X30" | 2.3469 | N | 15 |  | CH | 102 | 152 | 457.2 | 193.8 | 953 | 762 | 3 | Parallel | 13.5367 | 0.60279 | 2537.84 | 4.4646 | 5.184
279 | Kinectrics 2400 | 1734 | BOX GRND- 3 PH - 45"X30"X30" | 2.3521 | N | 15 |  | CH | 102 | 152 | 457.2 | 191.7 | 953 | 762 | 3 | Parallel | 13.61 | 0.62346 | 2528.9 | 4.7443 | 5.9535
280 | Kinectrics 2400 | 1735 | BOX GRND- 3 PH - 45"X30"X30" | 2.3503 | N | 15 |  | CH | 102 | 152 | 457.2 | 190.6 | 953 | 762 | 3 | Parallel | 13.73 | 0.59298 | 2448.05 | 4.5341 | 5.6835
281 | KEMA 2001 | Open | 4 / 08243 | 4.16 | N | 5.44 | 47.3828 | CH | 102 | 10000 | 483 | 215.4 | 10000 | 10000 | 3 | Parallel | 5.2767 | * | 2164 | 1.5043 | 1.7955
282 | KEMA 2001 | Open | 5 / 08244 | 4.16 | N | 5.44 | 47.3828 | CH | 102 | 10000 | 483 | 216.1 | 10000 | 10000 | 3 | Parallel | 5.3367 | * | 2284 | 1.3693 | 1.566
283 | KEMA 2001 | Cl | 7 / 08246 | 4.16 | N | 5.44 | 47.3828 | CH | 102 | 10000 | 483 | 216.9 | 10000 | 10000 | 3 | Parallel | 5.3433 | * | 2352 | 1.7589 | 2.1735
284 | KEMA 2001 | Cl | 8 / 08247 | 4.16 | N | 5.44 | 47.3828 | CH | 102 | 10000 | 483 | 213.6 | 10000 | 10000 | 3 | Parallel | 5.2167 | * | 2135 | 1.3134 | 1.62
285 | KEMA 2001 | Cl | 9 / 08248 | 4.16 | N | 5.44 | 47.3828 | CH | 102 | 10000 | 483 | 215.7 | 10000 | 10000 | 3 | Parallel | 5.2933 | * | 2416 | 1.6258 | 1.998
286 | KEMA 2001 | Open | 11/082410 | 4.16 | N | 6.11 | 43.0918 | CH | 102 | 10000 | 483 | 214.3 | 10000 | 10000 | 3 | Parallel | 5.83 |  | 2660 | 1.7338 | 2.052
287 | KEMA 2001 | Open | 12/082411 | 4.16 | N | 6.11 | 43.0918 | CH | 102 | 10000 | 483 | 214.9 | 10000 | 10000 | 3 | Parallel | 5.89 |  | 2658 | 1.7666 | 2.214
288 | KEMA 2001 | Open | 13/082412 | 4.16 | N | 6.11 | 43.0918 | CH | 102 | 10000 | 483 | 214.4 | 10000 | 10000 | 3 | Parallel | 5.88 |  | 2464 | 1.6991 | 1.971
289 | KEMA 2001 | Cl | 14/82413 | 4.16 | N | 6.11 | 43.0918 | CH | 102 | 10000 | 483 | 214.8 | 10000 | 10000 | 3 | Parallel | 5.93 |  | 2533 | 1.6624 | 1.9575
290 | KEMA 2001 | Cl | 15/8270 | 4.16 | N | 6.11 | 43.0918 | CH | 102 | 10000 | 483 | 215 | 10000 | 10000 | 3 | Parallel | 5.94 |  | 2580 | 1.4406 | 1.701
291 | KEMA 2001 | Cl | 16/8271 | 4.16 | N | 6.11 | 43.0918 | CH | 102 | 10000 | 483 | 214.9 | 10000 | 10000 | 3 | Parallel | 5.99 |  | 2606 | 1.8939 | 2.2275
292 | KEMA 2001 | Open | 19 / 8273 | 4.16 | N | 9.9467 |  | CH | 102 | 10000 | 610 | 214.8 | 10000 | 10000 | 3 | Parallel | 9.6867 | * | 4460 | 2.565 | 2.9835
293 | KEMA 2001 | Open | 20 / 8275 | 4.16 | N | 9.9467 |  | CH | 102 | 10000 | 610 | 215.7 | 10000 | 10000 | 3 | Parallel | 9.9467 | * | 4910 | 2.6904 | 3.3885
294 | KEMA 2001 | Cl | 21 / 8276 | 4.16 | N | 9.9467 |  | CH | 102 | 10000 | 610 | 215.9 | 10000 | 10000 | 3 | Parallel | 9.9833 | * | 4750 | 2.3625 | 2.6595
295 | KEMA 2001 | Cl | 24 / 82710 | 4.16 | N | 9.9467 |  | CH | 102 | 10000 | 610 | 214.8 | 10000 | 10000 | 3 | Parallel | 9.78 | * | 4660 | 2.7501 | 3.1995
296 | KEMA 2001 | Open | 27 / 82712 | 4.16 | N | 19.8333 | 36.3499 | CH | 102 | 10000 | 610 | 215.5 | 10000 | 10000 | 3 | Parallel | 18.4667 | * | 9880 | 5.6044 | 6.453
297 | KEMA 2001 | Open | 28 / 82713 | 4.16 | N | 19.8333 | 36.3499 | CH | 102 | 10000 | 610 | 215.7 | 10000 | 10000 | 3 | Parallel | 18.2333 | * | 9580 | 5.9477 | 7.155
298 | KEMA 2001 | Cl | 29 / 82714 | 4.16 | N | 19.8333 | 36.3499 | CH | 102 | 10000 | 610 | 215.9 | 10000 | 10000 | 3 | Parallel | 18.6333 | * | 9770 | 6.0673 | 7.0605
299 | KEMA 2001 | Cl | 30 / 82715 | 4.16 | N | 19.8333 | 36.3499 | CH | 102 | 10000 | 610 | 216.3 | 10000 | 10000 | 3 | Parallel | 18.8 | * | 10070 | 5.4424 | 6.4665
300 | KEMA 2001 | Cl | 31 / 8280 | 4.16 | N | 19.8333 | 36.3499 | CH | 102 | 10000 | 610 | 216.2 | 10000 | 10000 | 3 | Parallel | 23.0333 | * | 8890 | 5.8918 | 6.8715
301 | KEMA 2001 | Open | 34 / 8282 | 4.16 | N | 40.4333 | 25.1057 | CH | 102 | 10000 | 610 | 217.5 | 10000 | 10000 | 3 | Parallel | 38.4 | * | 19020 | 14.2232 | 17.199
302 | KEMA 2001 | Cl | 35 / 8283 | 4.16 | N | 40.4333 | 25.1057 | CH | 102 | 10000 | 610 | 216.5 | 10000 | 10000 | 3 | Parallel | 30 | * | 15390 | 14.3409 | 17.253
303 | KEMA 2001 | Cl | 36 / 8285 | 4.16 | N | 40.4333 | 25.1057 | CH | 102 | 10000 | 610 | 216.9 | 10000 | 10000 | 3 | Parallel | 38.0667 | * | 19770 | 15.1046 | 17.2935
304 | KEMA 2001 | Cl | 37 / 8286 | 4.16 | N | 40.4333 | 25.1057 | CH | 102 | 10000 | 610 | 217.3 | 10000 | 10000 | 3 | Parallel | 37.6333 | * | 20650 | 14.7111 | 17.3745
305 | KEMA 2001 | Cl | 39 / 82810 | 4.16 | N | 19.8333 | 36.3499 | CH | 102 | 10000 | 610 | 60.5 | 10000 | 10000 | 3 | Parallel | 19.5 | * | 2355 | 1.5043 | 1.809
306 | KEMA 2001 | Cl | 40 / 82811 | 4.16 | N | 19.8333 | 36.3499 | CH | 102 | 10000 | 610 | 54.5 | 10000 | 10000 | 3 | Parallel | 18.9333 | * | 2176 | 1.3172 | 1.5795
307 | KEMA 2001 | Cl | 41 / 8290 | 4.16 | N | 19.8333 | 36.3499 | CH | 102 | 10000 | 610 | 52 | 10000 | 10000 | 3 | Parallel | 19.2 | * | 2113 | 1.4117 | 1.6335
308 | KEMA 2001 | Open | 42 / 8291 | 4.16 | N | 19.8333 | 36.3499 | CH | 102 | 10000 | 610 | 102.9 | 10000 | 10000 | 3 | Parallel | 18.9 | * | 3990 | 2.6846 | 3.1725
309 | KEMA 2001 | Cl | 43 / 8292 | 4.16 | N | 19.8333 | 36.3499 | CH | 102 | 10000 | 610 | 102.8 | 10000 | 10000 | 3 | Parallel | 19.7667 | * | 4210 | 2.3972 | 2.8485
310 | KEMA 2001 | Cl | 44 / 8294 | 4.16 | N | 19.8333 | 36.3499 | CH | 102 | 10000 | 610 | 103 | 10000 | 10000 | 3 | Parallel | 19.3667 | * | 3970 | 2.2314 | 2.619
311 | KEMA 2001 | Cl | 45 / 8295 | 4.16 | N | 19.8333 | 36.3499 | CH | 102 | 10000 | 610 | 102.7 | 10000 | 10000 | 3 | Parallel | 19.5 | * | 4290 | 2.9604 | 3.5775
312 | KEMA 2001 | Open | 46 / 8296 | 4.16 | N | 19.8333 | 36.3499 | CH | 102 | 10000 | 610 | 508.3 | 10000 | 10000 | 3 | Parallel | 19.1333 | * | 20190 | 13.3592 | 15.8355
313 | KEMA 2001 | Cl | 47 / 8297 | 4.16 | N | 19.8333 | 36.3499 | CH | 102 | 10000 | 610 | 513.8 | 10000 | 10000 | 3 | Parallel | 19.4 | 1.5721 | 23160 | 14.4816 | 17.2125
314 | KEMA 2001 | Cl | 48 / 8298 | 4.16 | N | 19.8333 | 36.3499 | CH | 102 | 10000 | 610 | 513 | 10000 | 10000 | 3 | Parallel | 19.3667 | 1.4872 | 22220 | 13.7391 | 16.929
315 | KEMA 2001 | Cl | 49 / 8299 | 4.16 | N | 19.8333 | 36.3499 | CH | 102 | 10000 | 610 | 514.8 | 10000 | 10000 | 3 | Parallel | 19.4333 | 1.6119 | 23430 | 13.6639 | 16.821
316 | KEMA 2001 | Open | 56/8300 | 13.8 | N | 5.71 | 81.2947 | CH | 152 | 10000 | 762 | 205.4 | 10000 | 10000 | 3 | Parallel | 5.6167 | 1.5854 | 2771 | 1.0337 | 1.1205
317 | KEMA 2001 | Closed | 57/8301 | 13.8 | N | 5.71 | 81.2947 | CH | 152 | 10000 | 762 | 205.6 | 10000 | 10000 | 3 | Parallel | 5.6433 | 1.8861 | 2937 | 0.95657 | 1.0665
318 | KEMA 2001 | Closed | 58/8302 | 13.8 | N | 5.71 | 81.2947 | CH | 152 | 10000 | 762 | 207.1 | 10000 | 10000 | 3 | Parallel | 5.6933 | 1.758 | 2793 | 1.107 | 1.188
319 | KEMA 2001 | Closed | 59/8303 | 13.8 | N | 5.71 | 81.2947 | CH | 152 | 10000 | 762 | 207.6 | 10000 | 10000 | 3 | Parallel | 5.66 | 1.7297 | 2880 | 0.98357 | 1.107
320 | KEMA 2001 | Open | 60/8304 | 13.8 | N | 5.71 | 81.2947 | CH | 152 | 10000 | 762 | 205.7 | 10000 | 10000 | 3 | Parallel | 5.64 | 1.6321 | 2854 | 1.0376 | 1.1205
321 | KEMA 2001 | Open | 61/8305 | 13.8 | N | 10 | 89.2801 | CH | 152 | 10000 | 762 | 206.2 | 10000 | 10000 | 3 | Parallel | 9.99 | 1.7401 | * | 1.6566 | 1.9035
322 | KEMA 2001 | Closed | 62/8306 | 13.8 | N | 10 | 89.2801 | CH | 152 | 10000 | 762 | 205.6 | 10000 | 10000 | 3 | Parallel | 9.9267 | 1.7828 | 5480 | 1.836 | 1.9845
323 | KEMA 2001 | Closed | 63/8307 | 13.8 | N | 10 | 89.2801 | CH | 152 | 10000 | 762 | 206.5 | 10000 | 10000 | 3 | Parallel | 10.0267 | 1.777 | 5490 | 1.836 | 1.9845
324 | KEMA 2001 | Closed | 64/8308 | 13.8 | N | 10 | 89.2801 | CH | 152 | 10000 | 762 | 205.7 | 10000 | 10000 | 3 | Parallel | 10.03 | 1.6812 | 5160 | 1.7685 | 1.944
325 | KEMA 2001 | Open | 65/8309 | 13.8 | N | 20.1 | 51.0106 | CH | 152 | 10000 | 762 | 206.9 | 10000 | 10000 | 3 | Parallel | 20.2 | 1.5334 | 9300 | 4.1966 | 4.4685
326 | KEMA 2001 | Closed | 66/83010 | 13.8 | N | 20.1 | 51.0106 | CH | 152 | 10000 | 762 | 207.6 | 10000 | 10000 | 3 | Parallel | 20.0333 | 1.4913 | * | 3.5331 | 3.8475
327 | KEMA 2001 | Closed | 67/83011 | 13.8 | N | 20.1 | 51.0106 | CH | 152 | 10000 | 762 | 207.9 | 10000 | 10000 | 3 | Parallel | 20.1667 | 1.4786 | 8850 | 3.8591 | 4.158
328 | KEMA 2001 | Closed | 68/83012 | 13.8 | N | 20.1 | 51.0106 | CH | 152 | 10000 | 762 | 206.2 | 10000 | 10000 | 3 | Parallel | 20.1 | 1.4174 | 8450 | 2.6325 | 2.889
329 | KEMA 2001 | Open | 69/83013 | 13.8 | N | 40.8 | 33.769 | CH | 152 | 10000 | 762 | 207 | 10000 | 10000 | 3 | Parallel | 40 | 1.7181 | 18660 | 9.0816 | 9.8955
330 | KEMA 2001 | Closed | 70/83014 | 13.8 | N | 40.8 | 33.769 | CH | 152 | 10000 | 762 | 207.5 | 10000 | 10000 | 3 | Parallel | 40.4667 | 1.6633 | 18800 | 9.2591 | 10.233
331 | KEMA 2001 | Closed | 71/83015 | 13.8 | N | 40.8 | 33.769 | CH | 152 | 10000 | 762 | 208.7 | 10000 | 10000 | 3 | Parallel | 39.8667 | 1.6587 | 18700 | 9.4191 | 10.4625
332 | KEMA 2001 | Closed | 72/83016 | 13.8 | N | 40.8 | 33.769 | CH | 152 | 10000 | 762 | 206.6 | 10000 | 10000 | 3 | Parallel | 40.3333 | 1.6466 | 18690 | 9.7142 | 10.827
333 | KEMA 2001 | Closed | 73/83017 | 13.8 | N | 40.8 | 33.769 | CH | 152 | 10000 | 762 | 206.9 | 10000 | 10000 | 3 | Parallel | 40.4 | 1.7528 | 18900 | 9.9514 | 10.8945
334 | KEMA 2001 | Closed | 74/8310 | 13.8 | N | 20.1 | 51.0106 | CH | 152 | 10000 | 762 | 53.07 | 10000 | 10000 | 3 | Parallel | 19.8 | 1.837 | 3122 | 1.3384 | 1.4715
335 | KEMA 2001 | Closed | 76/8312 | 13.8 | N | 20.1 | 51.0106 | CH | 152 | 10000 | 762 | 53.06 | 10000 | 10000 | 3 | Parallel | 19.8 | 1.697 | 3092 | 0.99129 | 1.0935
336 | KEMA 2001 | Closed | 77/8313 | 13.8 | N | 20.1 | 51.0106 | CH | 152 | 10000 | 762 | 52.9 | 10000 | 10000 | 3 | Parallel | 19.8 | 1.776 | 3011 | 1.3577 | 1.512
337 | KEMA 2001 | Open | 78/8314 | 13.8 | N | 20.1 | 51.0106 | CH | 152 | 10000 | 762 | 104.6 | 10000 | 10000 | 3 | Parallel | 20 | 1.781 | 5400 | 2.3297 | 2.4975
338 | KEMA 2001 | Closed | 79/8315 | 13.8 | N | 20.1 | 51.0106 | CH | 152 | 10000 | 762 | 104.3 | 10000 | 10000 | 3 | Parallel | 20 | 1.784 | 5530 | 2.4339 | 2.6055
339 | KEMA 2001 | Closed | 80/8316 | 13.8 | N | 20.1 | 51.0106 | CH | 152 | 10000 | 762 | 104.5 | 10000 | 10000 | 3 | Parallel | 19.9 | 1.754 | 5320 | 2.3355 | 2.5245
340 | KEMA 2001 | Closed | 81/8317 | 13.8 | N | 20.1 | 51.0106 | CH | 152 | 10000 | 762 | 104.2 | 10000 | 10000 | 3 | Parallel | 20 | 1.632 | 5150 | 1.8379 | 2.187
341 | KEMA 2001 | Open | 82/8318 | 13.8 | N | 20.1 | 51.0106 | CH | 152 | 10000 | 762 | 252.4 | 10000 | 10000 | 3 | Parallel | 20 | 1.56 | 11060 | 4.7983 | 5.4405
342 | KEMA 2001 | Open | 83 | 13.8 | N | 20.1 | 51.0106 | CH | 152 | 10000 | 762 | 514.3 | 10000 | 10000 | 3 | Parallel | 20 | 1.453 | 20600 | 8.2524 | 9.045
343 | KEMA 2001 | Closed | 84 | 13.8 | N | 20.1 | 51.0106 | CH | 152 | 10000 | 762 | 516.4 | 10000 | 10000 | 3 | Parallel | 20.1 | 1.704 | 24670 | 10.8116 | 11.9475
344 | KEMA 2001 | Closed | 85 | 13.8 | N | 20.1 | 51.0106 | CH | 152 | 10000 | 762 | 515 | 10000 | 10000 | 3 | Parallel | 20 | 1.618 | 22960 | 9.4924 | 10.9755
345 | KEMA 2001 | Closed | 86 | 13.8 | N | 20.1 | 51.0106 | CH | 152 | 10000 | 762 | 514.8 | 10000 | 10000 | 3 | Parallel | 20.1 | 1.538 | 22180 | 8.532 | 9.4905
346 | KEMA 2001 | Open | 87 | 13.8 | N | 20.1 | 51.0106 | CH | 13 | 10000 | 762 | 206.2 | 10000 | 10000 | 3 | Parallel | 20.0667 | 0.5005 | 3018 | 0.86207 | 0.945
347 | KEMA 2001 | Open | 88 | 13.8 | N | 20.1 | 51.0106 | CH | 13 | 10000 | 762 | 206.5 | 10000 | 10000 | 3 | Parallel | 20.0333 | 0.53115 | 2639 | 0.918 | 1.0665
348 | KEMA 2001 | Closed | 89 | 13.8 | N | 20.1 | 51.0106 | CH | 13 | 10000 | 762 | 209.1 | 10000 | 10000 | 3 | Parallel | 20.2667 | 0.63103 | 3657 | 1.0993 | 1.2015
349 | KEMA 2001 | Closed | 90 | 13.8 | N | 20.1 | 51.0106 | CH | 13 | 10000 | 762 | 207.1 | 10000 | 10000 | 3 | Parallel | 20.1333 | 0.57791 | 3608 | 1.1745 | 1.512
350 | KEMA 2001 | Closed | 91 | 13.8 | N | 20.1 | 51.0106 | CH | 13 | 10000 | 762 | 209.5 | 10000 | 10000 | 3 | Parallel | 20.1667 | 0.6928 | 4080 | 1.2478 | 1.431

## Used Equip
All Tests at 21 kA BFC, 590 V Open ckt, 3 ph, calorimeters at 24" except as noted
Description | Breaker Trip or Fixed Duration Test | Arc Duration (msec) | Arc Current (Amperes) | Arc energy (kjoules) | Incident energy (cal/cm2) | I.E. for 200 msec
Used equipment test results -- Kinectrics Laboratory 2001
MCC unit, 600 V rated, fault on load side of 150A breaker at top of Nema size 5 contactor | Tripped | 6 | 3175 | 42 | 0.03 | 1
| Du | 6 | 2861 | 37 | 0.02 | 0.66667 | 0.03
| Du | 7 | 3638 | 38.8 | 0.02 | 0.57143 | 0.02
| Du | 6 | 2981 | 35.7 | 0.02 | 0.66667 | 0.02
| Du | 10 | 4291 | 47 | 0.03 | 0.6 | 0.02
| Du | 11 | 4233 | 46.6 | 0.03 | 0.54545 | 0.03
| Du | 11 | 4002 | 44 | 0.03 | 0.54545 | 0.03
| Du | 6 | 2620 | 35.6 | 0.02 | 0.66667 | 0.03
MCC unit Fault on line side of 30A breaker with 2 ft of #10 AWG wire to main bus | Fixed | 117 | 16213 | 934 | 0.6 | 1.0256 | 0.02
| Du | 115 | 17428 | 789 | 0.6 | 1.0435 | 0.6
MCC unit, fault on line side of 150A breaker in Size 5 unit, calorimeters at 18" | Fixed | 115 | 15546 | 783 | 0.6 | 1.0435 | 0.6
| Du | 115 | 16200 | 831 | 2.2 | 3.8261 | 0.6
600 V panelboard, fault on load side of 200A breaker | Tripped | 394 | 1251 | 180 | 0.7 | 0.35533 | 2.2
| Du | 22 | 1821 | 12.9 | 0.03 | 0.27273 | 0.7
| Du | 179 | 1779 | 102 | 0.3 | 0.3352 | 0.03
| Du | 292 | 1720 | 166 | 0.4 | 0.27397 | 0.3
| Du | 20 | 1670 | 14 | 0.03 | 0.3 | 0.4
600 V panelboard, fault on load side of 200A breaker on vertical bus (split bus power panel) | Tripped | 18 | 1544 | 12 | 0.03 | 0.33333 | 0.03
| Du | 134 | 340 | 25 | 0.05 | 0.074627 | 0.03
| Du | 129 | 1052 | 69 | 0.2 | 0.31008 | 0.05
| Du | 19 | 1239 | 10.9 | 0.02 | 0.21053 | 0.2
600 V panelboard, fault on line side (top) of vertical bus | Fixed | 217 | 16453 | 1340 | 3.3 | 3.0415 | 0.02
| Du | 210 | 16488 | 1162 | 3.1 | 2.9524 | 3.3
12" x 14" x 7.5" Deep Standard Box Test Results -- Square D Laboratory 2002
Test box, 1.5" electrode gaps, 1.5" electrode to box gaps | Fixed | 92.2867 | 18.11 | 637.6 | 1.4958 | 3.2416
Du | Du | 106.4 | 16.0233 | 901.2 | 2.3514 | 4.4199
Du | Du | 105.3667 | 15.9933 | 889.3 | 2.2714 | 4.3115
20" x 20" x 20" standard box test results -- Kinectrics Laboratory 2001
Test box with 10 mm electrode gaps, 102 mm electrode to box gaps | Fixed | 207 | 19.048 | 129 | 4.3478 | 4.2008
Du | Du | 211 | 18.831 | 128 | 3.981 | 3.7735
Du | Du | 211 | 18.919 | 126 | 4.0758 | 3.8633
Test box with 40 mm electrode gaps, 102 mm electrode to box gaps | Du | 209 | 16.459 | 193 | 5.5502 | 5.3112
Du | Du | 209 | 16.722 | 188 | 5.2632 | 5.0365
Du | Du | 209 | 16.924 | 183 | 5.7416 | 5.4944
Test box with 40 mm electrode gaps, 10 mm electrode to box gaps | Du | 212 | 17.356 | 166 | 8.5849 | 8.099
Du | Du | 208 | 17.532 | 166 | 8.1731 | 7.8587
Du | Du | 208 | 17.305 | 168 | 7.9808 | 7.6738
Test box with 10 mm electrode gaps, 10 mm electrode to box gaps | Du | 208 | 19.31 | 139 | 7.4038 | 7.1191
Du | Du | 213 | 19.071 | 134 | 7.6056 | 7.1414
Du | Du | 213 | 18.856 | 130 | 6.4789 | 6.0834