## Introduction
IEEE Std C57.139-2010 Guide for Dissolved Gas Analysis in Transformer Load Tap Changers Statistics Calculator
Prepared by the Fluids Subcommittee Working Group of the Transformers Committee
Cautions and Disclaimers
l | This information is based on technical data and procedures believed by the IEEE Std C57.139-2010 working group to be reliable.
l | The Guide and this calculator suggest approaches for conducting the statistical analysis of dissolved gas in transformer LTC oil but does not have mandatory requirements.
l | Following the suggestions in this guide does not guarantee diagnostic and repair decisions can be readily made. See Clause 1.3 in The Guide for a discussion of the limitations.
l | The DGA limits calculated in accordance with the procedures in The Guide are approximate. It is advisable to subject them to reasonableness checking before use, and to review their performance and adjust them as seems appropriate after they have been applied to real data.
l | These statistical procedures, and the DGA limits obtained by applying these procedures, should be used by persons competent to understand and perform the calculations and having expertise and experience in the application of dissolved-gas analysis to high-voltage equipment.
Summary of the methods
l | The distributions of concentrations of hydrogen, methane, ethane, ethylene, and acetylene encountered in LTC DGA are often irregular and highly variable in shape. For this reason, the method of deriving a Caution limit for such a gas or for total dissolved heating gas (TDHG) is to calculate an outlier rejection limit, based on the raw gas concentrations. The standard outlier rejection limit formula which is used here was originally published by the statistician John Tukey, a specialist in exploratory statistics and "robust" statistical analysis.
l | The distributions of combustible gas ratios used for LTC DGA, in particular ethylene/acetylene (C2H4/C2H2) and TDHG/acetylene (TDHG/C2H2), tend to fit a log-normal probability distribution. That fact is used to derive critical values for a statistical hypothesis test to be performed at the 5% significance level ("caution") and at the 1% significance level ("warning"). The null hypothesis H0 at both significance levels is "The observed ratio value is from the same distribution as the ratio values found in non-faulty LTCs of this type." The alternative hypothesis H1 is "The observed ratio value is so large that it is unlikely to belong to the same distribution as the ratio values found in non-faulty LTCs of this type." These critical values are used as the Caution and Warning limits, respectively, for the gas ratio.
l | Limits calculated according to these statistical methods have two advantages. First, they allow the evaluation of LTC DGA results to be conducted within a well-understood and widely-used statistical framework rather than by ad hoc methods. Second, the limits calculated according to these recommendations have lower "sampling variance" than percentiles, which have been widely recommended for the derivation of DGA limits. Lower sampling variance means that it is more likely that the derived value will perform well as a fault detection limit for new data.
Copyright
Copyright © 2010 by the Institute of Electrical and Electronics Engineers, Inc.
Three Park Avenue
New York, New York 10016-5997, USA
All rights reserved.
Published dd mmm 2010
Printed in the United States of America.
Print: ISBN
PDF: ISBN
No part of this publication may be reproduced in any form, in an electronic retrieval system or otherwise, without the prior written permission of the publisher.
The IEEE does not warrant or represent the accuracy or content of the material contained herein, and expressly disclaims any express or implied warranty, including any implied warranty of merchantability or fitness for a specific purpose, or that the use of the material contained herein is free from patent infringement. IEEE Standards documents are supplied “AS IS.”
USE AT YOUR OWN RISK.
Use of an IEEE Standard is wholly voluntary. The IEEE disclaims liability for any personal injury, property or other damage, of any nature whatsoever, whether special, indirect, consequential, or compensatory, directly or indirectly resulting from the publication, use of, or reliance upon this, or any other IEEE Standard document.
The existence of an IEEE Standard does not imply that there are no other ways to produce, test, measure, purchase, market, or provide other goods and services related to the scope of the IEEE Standard.
Furthermore, the viewpoint expressed at the time a standard is approved and issued is subject to change brought about through developments in the state of the art and comments received from users of the standard. Every IEEE Standard is subjected to review at least every five years for revision or reaffirmation.
When a document is more than five years old and has not been reaffirmed, it is reasonable to conclude that its contents, although still of some value, do not wholly reflect the present state of the art. Users are cautioned to check to determine that they have the latest edition of any IEEE Standard.
In publishing and making this document available, the IEEE is not suggesting or rendering professional or other services for, or on behalf of, any person or entity. Nor is the IEEE undertaking to perform any duty owed by any other person or entity to another.
Any person utilizing this, and any other IEEE Standards document, should rely upon the advice of a competent professional in determining the exercise of reasonable care in any given circumstances.
Interpretations: Occasionally questions may arise regarding the meaning of portions of standards as they relate to specific applications. When the need for interpretations is brought to the attention of IEEE, the Institute will initiate action to prepare appropriate responses.
Since IEEE Standards represent a consensus of concerned interests, it is important to ensure that any interpretation has also received the concurrence of a balance of interests.
For this reason, IEEE and the members of its societies and Standards Coordinating Committees are not able to provide an instant response to interpretation requests except in those cases where the matter has previously received formal consideration.

## Instructions
IEEE Std C57.139-2010 Guide for Dissolved Gas Analysis in Transformer Load Tap Changers Statistics Calculator
Prepared by the Fluids Subcommittee Working Group of the Transformers Committee
General Instructions for using this calculator
l | Refer to IEEE Std C57.139-2010 Guide for Dissolved Gas Analysis in Transformer Load Tap Changers (herein called The Guide), especially Annex B, for guidance on application and use of this calculator.
l | This workbook automates the calculation tasks and steps described in the Annexes using built-in Miscrosoft Excel functions and custom Visual Basic macros. Macros may not function in other spreadsheet products. Every attempt has been made to use built-in Excel functions where possible; however, some custom Visual Basic macros were necessary primarily because the number of rows of data to be analyzed is variable. Macros may take awhile to run, depending on the size of the data set.
l | The example data included on the Data SAMPLE tab are based on an electric utility data set of 726 samples for a single model of LTC (arcing in oil, single compartment, reactive, air breathing). These data are for illustrative use only and should not be used by the user for other purposes.
l | All worksheets have been protected to prevent accidental change of formulas; however, no password was used.
Entering Data on the "Data" worksheet
1 | At the top of the Data tab are fields where basic LTC information can be entered. There are fields for individual LTC models as well as generic models
2 | Above some columns of gas data is a field for the Minimum Reliable Value. This is considered to be 10 times the lab's detection limit. A typical good lab will have a detection limit of 1.0 μL/L. This data may be changed by the user if the user's lab has different detection limits
3 | Enter the gas data in the columns provided. If copying/pasting from another Excel workbook, use Paste-Special to preserve formatting
4 | Click the Calculate TDHG button
l | All Data are entered on the "Data" worksheet (sheet or tab)
Do NOT add or delete any rows above and including the header row otherwise most if not all of the macros will break
Do NOT add or delete any columns to the left of and including the last used column otherwise most if not all of the macros will break
Do NOT rearrange any of the rows or columns otherwise most if not all of the macros will break
l | Enter information & data only in cells with black font with a light blue background. Exception: The raw data has a white background color, not light blue
l | Blue font in a cell indicates calculated values, referenced values, or values not designed to be modified by the user. Do NOT enter anything is those cells
Entering Data and Running Calculations on the Gas Ratio worksheets
1 | Enter information & data only in cells with black font with a light blue background. Refer to the "Introduction" and "Ref" tab for definitions and abbreviations. Select Gas 1 and Gas 2 from the drop down menus. (Option) Enter User Defined Tolerance Bands
2 | Click the Run Gas Calculations button
3 | Click the Run Gas Ratio Calculations button (this macro may take a while to run)
4 | If additional Gas Ratio sheets are needed, just copy an existing one

## SAMPLE Data
IEEE Std C57.139-2010 Guide for Dissolved Gas Analysis in Transformer Load Tap Changers Statistics Calculator
SAMPLE DATA
|  | H2 | CH4 | C2H6 | C2H4 | C2H2 | CO | CO2 | O2 | N2
Equipment ID | Sample Date | Hydrogen | Methane | Ethane | Ethylene | Acetylene | Carbon Monoxide | Carbon Dioxide | Oxygen | Nitrogen
LTC04773 | 1997-07-24 | 20 | 0 | 0 | 4 | 38 | 76 | 501 | 25244 | 68031
LTC04773 | 1998-04-16 | 12 | 1 | 7 | 5 | 19 | 35 | 416 | 25583 | 67848
LTC04773 | 1999-07-19 | 16 | 2 | 0 | 3 | 25 | 191 | 546 | 9406 | 67332
LTC04773 | 2000-05-25 | 14 | 0 | 0 | 0 | 17 | 48 | 363 | 26015 | 69090
LTC04773 | 2001-06-19 | 25 | 2 | 0 | 0 | 20 | 46 | 424 | 21726 | 70109
LTC04773 | 2002-11-25 | 11 | 0 | 0 | 0 | 24 | 80 | 425 | 24276 | 66590
LTC04773 | 2003-06-26 | 21 | 0 | 0 | 11 | 29 | 106 | 501 | 22104 | 68343
LTC04774 | 1993-09-14 | 20 | 0 | 0 | 0 | 10 | 38 | 379 | 35156 | 70731
LTC04774 | 1994-06-01 | 7 | 0 | 5 | 2 | 0 | 23 | 383 | 28697 | 66399
LTC04774 | 1997-07-24 | 7 | 2 | 0 | 0 | 0 | 71 | 496 | 24780 | 67573
LTC04774 | 1998-04-16 | 7 | 0 | 0 | 0 | 0 | 0 | 391 | 28665 | 67359
LTC04774 | 1999-07-19 | 4 | 0 | 0 | 0 | 0 | 34 | 366 | 21866 | 67243
LTC04774 | 2000-05-25 | 4 | 0 | 1 | 1 | 0 | 11 | 388 | 30483 | 70206
LTC04774 | 2001-06-19 | 0 | 0 | 0 | 0 | 0 | 0 | 443 | 26134 | 67575
LTC04774 | 2003-06-26 | 3 | 0 | 0 | 0 | 0 | 28 | 402 | 27916 | 69855
LTC04774 | 2004-06-23 | 4 | 0 | 0 | 0 | 0 | 43 | 448 | 16511 | 65369
LTC04775 | 1993-09-14 | 36 | 0 | 15 | 74 | 40 | 43 | 472 | 28538 | 70171
LTC04775 | 1994-06-01 | 15 | 0 | 0 | 3 | 23 | 91 | 540 | 18280 | 76351
LTC04775 | 1997-07-24 | 19 | 0 | 0 | 6 | 57 | 76 | 505 | 27588 | 73766
LTC04775 | 1998-04-16 | 9 | 0 | 0 | 7 | 19 | 0 | 391 | 28737 | 67354
LTC04775 | 1999-07-19 | 21 | 1 | 0 | 3 | 26 | 150 | 518 | 13493 | 66247
LTC04775 | 2000-05-25 | 15 | 0 | 0 | 1 | 21 | 40 | 429 | 26193 | 65329
LTC04775 | 2001-06-19 | 21 | 1 | 0 | 4 | 25 | 80 | 463 | 17321 | 69896
LTC04775 | 2002-11-25 | 16 | 0 | 0 | 3 | 26 | 32 | 459 | 23731 | 66437
LTC04775 | 2003-06-26 | 18 | 0 | 0 | 5 | 30 | 87 | 519 | 24046 | 68696
LTC04775 | 2004-06-23 | 32 | 0 | 0 | 4 | 32 | 276 | 675 | 9590 | 71832
LTC04776 | 1993-09-14 | 34 | 0 | 0 | 4 | 42 | 20 | 368 | 33329 | 68537
LTC04776 | 1994-06-01 | 17 | 0 | 0 | 3 | 17 | 37 | 387 | 27033 | 68296
LTC04776 | 1998-04-16 | 11 | 0 | 0 | 4 | 18 | 0 | 422 | 28833 | 67609
LTC04776 | 1999-07-19 | 3 | 2 | 0 | 4 | 30 | 146 | 599 | 14536 | 66412
LTC04776 | 2000-05-25 | 48 | 0 | 0 | 4 | 18 | 58 | 408 | 24495 | 68456
LTC04776 | 2001-06-19 | 79 | 1 | 0 | 2 | 42 | 15 | 418 | 26146 | 67317
LTC04776 | 2003-06-26 | 20 | 0 | 0 | 5 | 36 | 90 | 437 | 23800 | 70370
LTC04776 | 2004-06-23 | 37 | 0 | 0 | 4 | 26 | 247 | 731 | 6736 | 65635
LTC06962 | 1993-09-08 | 14 | 0 | 0 | 2 | 14 | 64 | 541 | 26632 | 67683
LTC06962 | 1994-06-01 | 15 | 0 | 0 | 0 | 10 | 40 | 375 | 30952 | 68792
LTC06962 | 1998-10-28 | 16 | 0 | 0 | 1 | 9 | 3 | 459 | 24897 | 65234
LTC06962 | 1999-10-13 | 19 | 0 | 0 | 0 | 9 | 15 | 452 | 24904 | 62797
LTC06962 | 2000-11-15 | 12 | 0 | 5 | 0 | 0 | 124 | 702 | 8267 | 65059
LTC06962 | 2001-11-14 | 15 | 2 | 4 | 1 | 0 | 35 | 476 | 20637 | 59399
LTC06962 | 2002-11-04 | 19 | 0 | 0 | 1 | 7 | 0 | 491 | 28279 | 73152
LTC06962 | 2003-10-13 | 18 | 0 | 0 | 1 | 0 | 32 | 471 | 25338 | 63558
LTC06962 | 2004-10-25 | 5 | 0 | 0 | 0 | 0 | 13 | 372 | 28414 | 74024
LTC06963 | 1993-09-22 | 77 | 0 | 0 | 28 | 238 | 22 | 464 | 33759 | 73632
LTC06963 | 1997-06-24 | 65 | 5 | 0 | 18 | 144 | 134 | 595 | 26659 | 74595
LTC06963 | 1998-10-22 | 110 | 17 | 0 | 14 | 171 | 48 | 400 | 22520 | 58508
LTC06963 | 1999-08-04 | 133 | 28 | 0 | 50 | 447 | 0 | 393 | 26412 | 63104
LTC06963 | 2000-10-10 | 136 | 23 | 4 | 58 | 5.2 | 28 | 439 | 28842 | 66062
LTC06963 | 2002-11-01 | 135 | 25 | 5 | 72 | 604 | 64 | 509 | 30420 | 71367
LTC06963 | 2003-09-05 | 133 | 18 | 2 | 64 | 506 | 17 | 391 | 29614 | 68737
LTC06963 | 2004-08-17 | 19 | 4 | 1 | 26 | 100 | 26 | 463 | 35149 | 81865
LTC07145 | 1993-09-14 | 59 | 0 | 0 | 10 | 102 | 74 | 617 | 22553 | 68279
LTC07145 | 1994-06-01 | 39 | 0 | 5 | 10 | 69 | 50 | 395 | 29477 | 68912
LTC07145 | 1997-07-18 | 117 | 10 | 2 | 18 | 168 | 264 | 934 | 11139 | 68990
LTC07145 | 1998-09-02 | 30 | 5 | 0 | 21 | 60 | 13 | 349 | 28200 | 68133
LTC07145 | 1999-09-03 | 29 | 3 | 0 | 5 | 55 | 29 | 498 | 25987 | 67796
LTC07145 | 2000-08-23 | 18 | 2 | 0 | 6 | 45 | 14 | 344 | 23278 | 65187
LTC07145 | 2002-10-16 | 19 | 0 | 0 | 6 | 38 | 0 | 329 | 27275 | 66162
LTC07145 | 2003-12-18 | 18 | 0 | 0 | 1 | 47 | 11 | 378 | 31164 | 70312
LTC07145 | 2004-08-27 | 16 | 2 | 0 | 6 | 44 | 19 | 321 | 31310 | 76711
LTC07146 | 1993-09-08 | 10 | 0 | 0 | 6 | 36 | 80 | 406 | 27816 | 68014
LTC07146 | 1994-06-10 | 23 | 0 | 0 | 7 | 55 | 141 | 465 | 29020 | 72506
LTC07146 | 1998-06-17 | 42 | 6 | 0 | 13 | 69 | 36 | 424 | 26882 | 69785
LTC07146 | 1999-07-20 | 26 | 2 | 0 | 4 | 24 | 38 | 396 | 25232 | 68086
LTC07146 | 2000-07-03 | 4 | 0 | 0 | 0 | 0 | 38 | 387 | 26821 | 71981
LTC07146 | 2002-09-04 | 18 | 0 | 0 | 1 | 4 | 94 | 472 | 26707 | 67088
LTC07146 | 2003-09-02 | 10 | 0 | 1 | 0 | 6 | 32 | 387 | 28100 | 72528
LTC07146 | 2004-08-18 | 8 | 1 | 0 | 0 | 0 | 63 | 447 | 27317 | 76820
LTC08077 | 1993-09-07 | 45 | 0 | 0 | 18 | 157 | 42 | 337 | 27768 | 58216
LTC08077 | 1993-10-12 | 32 | 0 | 3 | 22 | 145 | 49 | 526 | 31353 | 69326
LTC08077 | 1994-06-14 | 28 | 0 | 0 | 15 | 97 | 38 | 418 | 34991 | 80183
LTC08077 | 1997-07-01 | 35 | 4 | 3 | 19 | 115 | 87 | 499 | 26895 | 70920
LTC08077 | 1998-09-01 | 41 | 6 | 0 | 16 | 131 | 152 | 536 | 20697 | 68623
LTC08077 | 1999-09-09 | 48 | 9 | 0 | 20 | 150 | 14 | 368 | 27733 | 64408
LTC08077 | 2000-08-29 | 46 | 7 | 0 | 18 | 161 | 0 | 358 | 28576 | 66137
LTC08077 | 2001-10-19 | 18 | 11 | 0 | 23 | 107 | 29 | 380 | 13290 | 41369
LTC08077 | 2002-10-23 | 26 | 5 | 0 | 19 | 121 | 0 | 328 | 32352 | 71115
LTC08077 | 2003-09-18 | 40 | 6 | 0 | 21 | 171 | 25 | 422 | 25840 | 65399
LTC08077 | 2004-09-15 | 22 | 4 | 0 | 14 | 87 | 12 | 341 | 30251 | 70186
LTC08077 | 2006-03-08 | 3 | 5 | 0 | 12 | 6 | 24 | 454 | 19505 | 52886
LTC09580 | 1993-08-16 | 23 | 0 | 0 | 23 | 73 | 48 | 613 | 30624 | 84808
LTC09580 | 2000-02-01 | 23 | 6 | 0 | 20 | 128 | 6 | 408 | 28585 | 64151
LTC09580 | 2001-03-13 | 20 | 3 | 0 | 14 | 101 | 38 | 383 | 28002 | 67699
LTC09580 | 2001-10-30 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 22963 | 70144
LTC09580 | 2002-02-22 | 8 | 0 | 0 | 0 | 16 | 39 | 353 | 24882 | 59377
LTC09580 | 2004-02-13 | 24 | 0 | 0 | 8 | 79 | 8 | 392 | 29086 | 64400
LTC09580 | 2005-02-04 | 5 | 0 | 2 | 1 | 13 | 6 | 383 | 28069 | 63241
LTC09580 | 2006-03-20 | 4 | 3 | 0 | 2 | 0 | 20 | 501 | 22411 | 59406
LTC09844 | 1993-09-22 | 208 | 0 | 6 | 38 | 410 | 0 | 508 | 23735 | 67533
LTC09844 | 1996-03-13 | 25 | 5 | 0 | 10 | 110 | 36 | 466 | 29372 | 63843
LTC09844 | 1997-05-08 | 47 | 4 | 0 | 13 | 143 | 8 | 470 | 30672 | 69856
LTC09844 | 1998-06-23 | 13 | 0 | 1 | 3 | 16 | 28 | 442 | 26959 | 73704
LTC09844 | 2000-07-25 | 5 | 0 | 0 | 0 | 11 | 0 | 328 | 27894 | 70304
LTC09844 | 2001-10-11 | 26 | 12 | 0 | 25 | 142 | 259 | 663 | 9535 | 47805
LTC09844 | 2002-11-25 | 181 | 2 | 2 | 4 | 17 | 225 | 891 | 7824 | 77531
LTC09844 | 2003-09-15 | 216 | 0 | 0 | 2 | 14 | 181 | 1001 | 17888 | 76923
LTC09844 | 2004-10-06 | 90 | 0 | 0 | 2 | 9 | 138 | 842 | 22022 | 72070
LTC09846 | 1993-09-07 | 232 | 531 | 3 | 48 | 384 | 122 |  | 29422 | 95007
LTC09846 | 1993-10-12 | 374 | 17 | 5 | 93 | 759 | 161 | 875 | 10215 | 67692
LTC09846 | 1994-06-14 | 74 | 0 | 0 | 4 | 60 | 101 | 622 | 30599 | 77426
LTC09846 | 1996-04-08 | 88 | 20 | 5 | 30 | 152 | 35 | 518 | 29846 | 65891
LTC09846 | 1997-05-23 | 36 | 3 | 0 | 12 | 76 | 73 | 617 | 23150 | 60163
LTC09846 | 1998-05-01 | 16 | 2 | 6 | 5 | 31 | 28 | 413 | 28671 | 67595
LTC09846 | 1999-05-24 | 9 | 0 | 0 | 0 | 0 | 47 | 500 | 25154 | 70910
LTC09846 | 2000-05-05 | 7 | 0 | 0 | 2 | 0 | 27 | 439 | 28876 | 70430
LTC09846 | 2002-06-18 | 0 | 0 | 0 | 0 | 0 | 0 | 324 | 30334 | 70492
LTC09846 | 2003-05-28 | 14 | 4 | 0 | 5 | 24 | 12 | 334 | 29084 | 68495
LTC09846 | 2005-06-17 | 35 | 0 | 3 | 15 | 104 | 19 | 352 | 37137 | 68456
LTC10044 | 1993-09-30 | 76 | 0 | 2 | 13 | 82 | 77 | 480 | 30595 | 71366
LTC10044 | 1994-06-15 | 61 | 0 | 5 | 10 | 54 | 102 | 647 | 26677 | 69958
LTC10044 | 1997-05-14 | 46 | 0 | 4 | 5 | 41 | 63 | 663 | 23706 | 70305
LTC10044 | 1999-06-08 | 29 | 0 | 0 | 5 | 8 | 165 | 684 | 16593 | 72371
LTC10044 | 2000-04-27 | 23 | 0 | 0 | 3 | 22 | 57 | 595 | 23517 | 68177
LTC10044 | 2002-06-25 | 63 | 0 | 0 | 8 | 34 | 40 | 526 | 25638 | 69727
LTC10044 | 2003-06-09 | 47 | 0 | 2 | 7 | 26 | 91 | 592 | 22735 | 70132
LTC10044 | 2004-05-18 | 20 | 0 | 0 | 4 | 6 | 66 | 484 | 26589 | 67851
LTC10044 | 2005-05-26 | 36 | 0 | 4 | 10 | 33 | 99 | 481 | 26144 | 69611
LTC10044 | 2006-05-15 | 28 | 8 | 3 | 14 | 38 | 80 | 663 | 18998 | 62399
LTC10098 | 1993-08-17 | 50 | 0 | 0 | 0 | 0 | 125 | 79 | 27110 | 71405
LTC10098 | 1994-06-23 | 44 | 0 | 0 | 9 | 51 | 110 | 627 | 26332 | 65851
LTC10098 | 1995-08-14 | 172 | 20 | 7 | 22 | 178 | 238 | 955 | 26215 | 72939
LTC10098 | 1996-03-05 | 16 | 1 | 2 | 6 | 38 | 72 | 640 | 27058 | 68950
LTC10098 | 1997-05-21 | 50 | 6 | 3 | 16 | 102 | 132 | 766 | 25966 | 70005
LTC10098 | 1998-03-16 | 20 | 0 | 0 | 6 | 43 | 19 | 418 | 28799 | 69318
LTC10098 | 1999-04-13 | 10 | 3 | 0 | 5 | 22 | 0 | 309 | 29570 | 68208
LTC10098 | 2000-03-30 | 5 | 0 | 0 | 0 | 7 | 13 | 345 | 29354 | 66291
LTC10098 | 2001-05-24 | 9 | 2 | 0 | 3 | 14 | 9 | 357 | 27348 | 67287
LTC10098 | 2002-05-15 | 6 | 0 | 0 | 6 | 19 | 8 | 336 | 32137 | 74463
LTC10098 | 2003-05-29 | 12 | 0 | 0 | 4 | 29 | 0 | 336 | 28922 | 66109
LTC10098 | 2004-05-05 | 11 | 0 | 0 | 5 | 20 | 8 | 312 | 29193 | 70482
LTC10098 | 2005-05-19 | 18 | 0 | 0 | 8 | 38 | 0 | 314 | 29261 | 69970
LTC10121 | 2001-03-14 | 66 | 28 | 15 | 174 | 554 | 55 | 819 | 26982 | 65750
LTC10121 | 2001-11-19 | 0 | 14 | 0 | 1 | 0 | 16 | 295 | 20964 | 51995
LTC10121 | 2002-03-07 | 88 | 36 | 4 | 83 | 368 | 12 | 419 | 26269 | 61776
LTC10121 | 2003-04-10 | 103 | 61 | 15 | 245 | 923 | 46 | 779 | 26582 | 60880
LTC10121 | 2004-03-23 | 144 | 74 | 20 | 294 | 1082 | 57 | 944 | 27924 | 71925
LTC10121 | 2005-03-21 | 403 | 192 | 57 | 815 | 2602 | 61 | 1106 | 29603 | 70010
LTC10121 | 2006-03-20 | 65 | 34 | 5 | 71 | 390 | 27 | 491 | 21535 | 60911
LTC10131 | 1993-08-17 | 73 | 0 | 0 | 14 | 73 | 172 | 858 | 22530 | 71258
LTC10131 | 1994-06-10 | 49 | 0 | 0 | 7 | 53 | 237 | 709 | 24989 | 70274
LTC10131 | 1995-08-04 | 90 | 14 | 0 | 19 | 152 | 158 | 806 | 29059 | 81089
LTC10131 | 1996-03-13 | 98 | 4 | 0 | 11 | 60 | 60 | 537 | 34028 | 76285
LTC10131 | 1997-05-22 | 55 | 4 | 2 | 16 | 101 | 49 | 507 | 30611 | 69385
LTC10131 | 1998-02-13 | 63 | 13 | 16 | 28 | 144 | 33 | 418 | 28914 | 71235
LTC10131 | 1999-03-25 | 22 | 2 | 1 | 3 | 15 | 32 | 431 | 27830 | 67405
LTC10131 | 2000-03-08 | 32 | 0 | 0 | 4 | 16 | 42 | 522 | 27270 | 70222
LTC10131 | 2001-03-14 | 27 | 2 | 0 | 3 | 43 | 46 | 483 | 25293 | 67636
LTC10131 | 2002-03-06 | 51 | 0 | 0 | 3 | 27 | 42 | 624 | 24389 | 65076
LTC10131 | 2003-04-09 | 28 | 1 | 0 | 4 | 2 | 58 | 367 | 23644 | 58583
LTC10131 | 2004-03-18 | 43 | 0 | 1 | 3 | 21 | 101 | 637 | 21111 | 67906
LTC10131 | 2005-03-18 | 32 | 0 | 0 | 5 | 28 | 64 | 507 | 25108 | 67589
LTC10131 | 2006-03-20 | 68 | 7 | 0 | 8 | 37 | 61 | 671 | 22872 | 65653
LTC10145 | 1993-08-17 | 27 | 0 | 12 | 55 | 34 | 69 | 476 | 28547 | 69261
LTC10145 | 1994-05-25 | 24 | 0 | 0 | 9 | 38 | 46 | 370 | 30749 | 68030
LTC10145 | 1994-06-23 | 25 | 0 | 0 | 10 | 43 | 65 | 363 | 34164 | 79713
LTC10145 | 1994-07-26 | 12 | 0 | 6 | 10 | 43 | 56 | 420 | 32383 | 74087
LTC10145 | 1994-08-24 | 14 | 0 | 0 | 13 | 37 | 80 | 500 | 26499 | 66943
LTC10145 | 1995-08-09 | 16 | 3 | 0 | 7 | 56 | 120 | 544 | 26474 | 68786
LTC10145 | 1996-03-04 | 4 | 2 | 0 | 6 | 31 | 49 | 549 | 30080 | 69283
LTC10145 | 1997-05-21 | 28 | 4 | 1 | 16 | 81 | 49 | 486 | 29110 | 70383
LTC10145 | 1998-07-30 | 40 | 7 | 1 | 13 | 60 | 74 | 571 | 27305 | 76031
LTC10145 | 1999-08-05 | 7 | 0 | 0 | 2 | 11 | 0 | 283 | 25748 | 68317
LTC10145 | 2000-07-27 | 5 | 0 | 0 | 0 | 5 | 0 | 269 | 27286 | 64518
LTC10145 | 2002-10-04 | 11 | 0 | 0 | 3 | 12 | 0 | 296 | 26669 | 61358
LTC10145 | 2003-09-02 | 11 | 0 | 1 | 0 | 18 | 20 | 296 | 29533 | 70139
LTC10145 | 2004-08-30 | 12 | 3 | 0 | 3 | 17 | 11 | 305 | 31462 | 75578
LTC10158 | 1990-06-15 | 65 | 0 | 0 | 7 | 38 | 156 | 732 | 21864 | 72854
LTC10158 | 1990-09-07 | 60 | 0 | 0 | 8 | 39 | 38 | 539 | 28828 | 66744
LTC10158 | 1996-03-12 | 19 | 0 | 0 | 4 | 29 | 26 | 658 | 60462 | 177308
LTC10158 | 1997-05-22 | 42 | 3 | 2 | 11 | 76 | 35 | 502 | 26381 | 68141
LTC10158 | 1997-08-08 | 92 | 8 | 0 | 19 | 158 | 158 | 656 | 26918 | 69107
LTC10158 | 1998-01-30 | 47 | 6 | 0 | 12 | 98 | 32 | 438 | 27028 | 67237
LTC10158 | 1998-03-10 | 58 | 6 | 0 | 18 | 117 | 70 | 590 | 21185 | 68171
LTC10158 | 1999-02-17 | 27 | 4 | 0 | 5 | 44 | 43 | 465 | 21715 | 63510
LTC10158 | 1999-05-19 | 25 | 3 | 0 | 35 | 35 | 45 | 492 | 25238 | 71116
LTC10158 | 2000-03-28 | 23 | 0 | 1 | 0 | 9 | 36 | 436 | 27856 | 71665
LTC10158 | 2001-04-23 | 33 | 0 | 0 | 4 | 26 | 10 | 631 | 25207 | 69285
LTC10158 | 2002-08-01 | 75 | 0 | 4 | 4 | 28 | 217 | 1037 | 13371 | 67076
LTC10158 | 2003-05-28 | 54 | 0 | 0 | 2 | 30 | 131 | 740 | 20544 | 71690
LTC10158 | 2004-05-05 | 42 | 0 | 0 | 1 | 1 | 85 | 562 | 22671 | 65012
LTC10158 | 2005-06-06 | 10 | 0 | 0 | 3 | 16 | 8 | 324 | 28852 | 72374
LTC10158 | 2006-05-17 | 21 | 2 | 0 | 2 | 15 | 10 | 353 | 20894 | 55257
LTC10171 | 1993-08-17 | 276 | 1833 | 505 | 3731 | 149 | 428 | 1211 | 17155 | 74832
LTC10171 | 1993-08-26 | 280 | 2026 | 588 | 4434 | 163 | 439 | 979 | 24893 | 81857
LTC10171 | 1993-09-03 | 375 | 3802 | 1422 | 8343 | 211 | 476 | 1084 | 23162 | 77896
LTC10171 | 1993-09-13 | 445 | 4449 | 1736 | 10526 | 274 | 1113 | 822 | 28761 | 77418
LTC10171 | 1993-09-21 | 469 | 5440 | 2173 | 13424 | 360 | 372 | 783 | 26493 | 82095
LTC10171 | 1994-05-26 | 18 | 0 | 0 | 6 | 36 | 0 | 443 | 32792 | 69117
LTC10171 | 1994-06-23 | 27 | 0 | 0 | 9 | 56 | 21 | 341 | 31627 | 68516
LTC10171 | 1994-07-26 | 11 | 0 | 0 | 10 | 48 | 19 | 346 | 32079 | 70200
LTC10171 | 1994-08-24 | 13 | 0 | 7 | 9 | 30 | 46 | 351 | 32980 | 70051
LTC10171 | 1995-08-14 | 25 | 5 | 0 | 16 | 80 | 19 | 367 | 32499 | 72038
LTC10171 | 1996-02-26 | 9 | 2 | 1 | 10 | 58 | 29 | 481 | 31482 | 67872
LTC10171 | 1997-05-21 | 20 | 3 | 0 | 14 | 62 | 47 | 558 | 29932 | 72162
LTC10171 | 1998-07-30 | 35 | 4 | 0 | 17 | 43 | 125 | 585 | 17905 | 73988
LTC10171 | 1999-08-09 | 18 | 3 | 0 | 8 | 35 | 71 | 398 | 26836 | 77637
LTC10171 | 2000-07-27 | 3 | 0 | 0 | 0 | 0 | 0 | 426 | 28107 | 66279
LTC10171 | 2002-10-03 | 8 | 0 | 0 | 3 | 9 | 0 | 329 | 26338 | 66807
LTC10171 | 2003-09-03 | 22 | 0 | 2 | 17 | 51 | 0 | 291 | 28558 | 65259
LTC10171 | 2004-08-30 | 12 | 2 | 0 | 4 | 12 | 11 | 296 | 30642 | 74794
LTC10184 | 1993-08-17 | 126 | 0 | 10 | 20 | 119 | 179 | 964 | 17630 | 65302
LTC10184 | 1994-06-10 | 91 | 0 | 9 | 15 | 102 | 219 | 718 | 23779 | 69088
LTC10184 | 1995-08-04 | 0 | 10 | 12 | 11 | 50 | 27 | 444 | 34376 | 82087
LTC10184 | 1996-03-13 | 139 | 12 | 2 | 22 | 164 | 17 | 440 | 30095 | 68993
LTC10184 | 1997-06-05 | 38 | 4 | 0 | 11 | 82 | 0 | 428 | 28405 | 67400
LTC10184 | 1998-11-02 | 53 | 5 | 0 | 7 | 50 | 13 | 397 | 25919 | 68654
LTC10184 | 1999-10-20 | 78 | 5 | 0 | 10 | 65 | 18 | 417 | 24105 | 62804
LTC10184 | 2000-12-04 | 234 | 3 | 0 | 8 | 50 | 80 | 623 | 21229 | 71948
LTC10184 | 2001-05-24 | 357 | 5 | 0 | 6 | 68 | 182 | 780 | 15601 | 77225
LTC10184 | 2001-10-25 | 140 | 13 | 0 | 22 | 104 | 102 | 746 | 8856 | 37845
LTC10184 | 2002-12-04 | 138 | 4 | 0 | 10 | 66 | 0 | 440 | 27360 | 72887
LTC10184 | 2003-11-03 | 41 | 3 | 0 | 4 | 22 | 57 | 487 | 30209 | 78078
LTC10184 | 2004-10-26 | 50 | 2 | 0 | 3 | 20 | 41 | 465 | 30868 | 75896
LTC10185 | 1993-08-13 | 56 | 0 | 0 | 9 | 63 | 107 | 625 | 30216 | 76411
LTC10185 | 1994-06-07 | 34 | 0 | 0 | 8 | 36 | 84 | 454 | 27559 | 67693
LTC10185 | 1995-08-16 | 72 | 5 | 0 | 13 | 67 | 156 | 745 | 27077 | 70199
LTC10185 | 1996-03-20 | 27 | 0 | 0 | 11 | 37 | 27 | 573 | 34077 | 73711
LTC10185 | 1997-05-27 | 18 | 0 | 0 | 5 | 30 | 40 | 540 | 29098 | 68483
LTC10185 | 1998-07-23 | 95 | 4 | 0 | 12 | 42 | 176 | 1370 | 12597 | 69420
LTC10185 | 1999-06-18 | 42 | 47 | 3 | 27 | 37 | 119 | 567 | 29984 | 84401
LTC10185 | 1999-08-03 | 286 | 1366 | 508 | 3969 | 263 | 508 | 988 | 19001 | 67017
LTC10185 | 1999-08-13 | 7 | 0 | 0 | 2 | 9 | 0 | 350 | 25057 | 61470
LTC10185 | 1999-08-20 | 12 | 0 | 0 | 2 | 17 | 0 | 291 | 26978 | 64763
LTC10185 | 1999-10-26 | 4 | 0 | 0 | 0 | 0 | 0 | 367 | 22583 | 60605
LTC10185 | 2000-06-13 | 3 | 0 | 4 | 1 | 0 | 0 | 285 | 28652 | 68954
LTC10185 | 2002-07-11 | 3 | 0 | 0 | 1 | 9 | 6 | 219 | 25004 | 69277
LTC10185 | 2003-07-18 | 6 | 0 | 0 | 2 | 10 | 0 | 296 | 25454 | 62798
LTC10185 | 2004-06-24 | 6 | 0 | 0 | 1 | 6 | 0 | 277 | 26074 | 61441
LTC10185 | 2005-06-23 | 5 | 0 | 0 | 3 | 4 | 14 | 301 | 28528 | 67998
LTC10195 | 1993-08-17 | 52 | 0 | 0 | 8 | 56 | 92 | 572 | 28886 | 68687
LTC10195 | 1994-05-26 | 62 | 0 | 0 | 7 | 53 | 170 | 499 | 26813 | 67274
LTC10195 | 1994-06-23 | 60 | 0 | 0 | 8 | 57 | 128 | 648 | 26378 | 69619
LTC10195 | 1994-07-26 | 60 | 0 | 0 | 23 | 73 | 108 | 609 | 29594 | 72395
LTC10195 | 1994-08-24 | 54 | 0 | 0 | 8 | 64 | 98 | 703 | 30256 | 72939
LTC10195 | 1995-08-14 | 75 | 4 | 0 | 14 | 68 | 168 | 759 | 25236 | 70999
LTC10195 | 1996-03-05 | 15 | 2 | 0 | 5 | 40 | 46 | 601 | 29945 | 70766
LTC10195 | 1997-05-21 | 42 | 5 | 3 | 18 | 44 | 35 | 618 | 31690 | 72189
LTC10195 | 1998-04-16 | 39 | 3 | 2 | 7 | 46 | 25 | 437 | 26277 | 72794
LTC10195 | 1999-06-16 | 71 | 10 | 4 | 18 | 99 | 99 | 574 | 22826 | 64080
LTC10195 | 2000-05-16 | 112 | 13 | 0 | 26 | 146 | 79 | 491 | 24981 | 65235
LTC10195 | 2001-06-14 | 53 | 2 | 0 | 11 | 35 | 104 | 636 | 23924 | 71246
LTC10195 | 2002-06-12 | 54 | 6 | 1 | 19 | 90 | 0 | 762 | 20913 | 68683
LTC10195 | 2003-06-04 | 54 | 6 | 0 | 9 | 46 | 93 | 637 | 21568 | 70189
LTC10195 | 2004-06-02 | 85 | 4 | 0 | 10 | 42 | 103 | 642 | 24814 | 67098
LTC10195 | 2004-09-23 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 16325 | 83040
LTC10195 | 2005-05-25 | 18 | 0 | 2 | 6 | 34 | 19 | 405 | 26500 | 69319
LTC10216 | 1993-08-16 | 21 | 0 | 3 | 6 | 22 | 59 | 571 | 24901 | 76718
LTC10216 | 1994-06-07 | 11 | 0 | 0 | 5 | 39 | 53 | 408 | 23174 | 66828
LTC10216 | 1995-08-16 | 28 | 4 | 0 | 9 | 49 | 82 | 671 | 28577 | 69930
LTC10216 | 1996-04-10 | 4 | 0 | 0 | 0 | 28 | 44 | 544 | 26838 | 74976
LTC10216 | 1997-05-23 | 12 | 4 | 0 | 5 | 61 | 125 | 800 | 15642 | 72985
LTC10216 | 1998-01-29 | 9 | 0 | 0 | 3 | 21 | 22 | 367 | 25502 | 66793
LTC10216 | 1999-03-02 | 3 | 0 | 1 | 2 | 2 | 23 | 431 | 27243 | 66605
LTC10216 | 2000-02-28 | 6 | 0 | 0 | 2 | 6 | 11 | 394 | 28733 | 68006
LTC10216 | 2001-04-10 | 4 | 0 | 0 | 2 | 4 | 0 | 320 | 26886 | 59051
LTC10216 | 2002-01-28 | 3 | 4 | 0 | 0 | 4 | 0 | 313 | 27668 | 60731
LTC10216 | 2003-03-11 | 13 | 0 | 0 | 10 | 14 | 0 | 423 | 25953 | 58652
LTC10216 | 2003-03-18 | 8 | 0 | 0 | 8 | 12 | 0 | 414 | 27404 | 61013
LTC10216 | 2004-02-10 | 7 | 0 | 0 | 3 | 9 | 13 | 366 | 30140 | 64732
LTC10216 | 2004-03-26 | 2 | 0 | 0 | 2 | 4 | 0 | 327 | 27278 | 60135
LTC10216 | 2004-06-15 | 4 | 3 | 0 | 0 | 0 | 1 | 319 | 26862 | 66975
LTC10216 | 2005-02-28 | 8 | 0 | 0 | 3 | 3 | 12 | 356 | 29923 | 65768
LTC10267 | 1993-09-07 | 54 | 0 | 0 | 1 | 22 | 118 | 661 | 27770 | 73682
LTC10267 | 1994-06-16 | 105 | 0 | 7 | 19 | 120 | 153 | 869 | 22099 | 74019
LTC10267 | 1996-04-09 | 117 | 8 | 1 | 15 | 118 | 143 | 1024 | 15536 | 62058
LTC10267 | 1997-05-15 | 70 | 4 | 0 | 8 | 86 | 209 | 1080 | 7169 | 65114
LTC10267 | 1998-03-26 | 51 | 4 | 0 | 17 | 98 | 34 | 479 | 24000 | 59981
LTC10267 | 1999-09-30 | 11 | 0 | 0 | 0 | 5 | 0 | 338 | 28269 | 66562
LTC10267 | 2000-10-10 | 22 | 2 | 0 | 5 | 49 | 0 | 376 | 29155 | 64277
LTC10267 | 2001-11-12 | 37 | 7 | 0 | 3 | 13 | 45 | 527 | 24442 | 64944
LTC10267 | 2002-10-23 | 6 | 0 | 0 | 2 | 14 | 0 | 336 | 32621 | 70859
LTC10267 | 2003-09-30 | 3 | 0 | 0 | 1 | 0 | 19 | 504 | 30042 | 69561
LTC10267 | 2004-09-29 | 0 | 0 | 3 | 0 | 0 | 8 | 445 | 28875 | 70235
LTC10289 | 1993-08-16 | 387 | 2794 | 1214 | 7709 | 222 | 134 | 435 | 32951 | 79720
LTC10289 | 1993-08-20 | 416 | 2952 | 1235 | 8733 | 301 | 70 | 442 | 27658 | 73425
LTC10289 | 1993-08-28 | 513 | 4520 | 2042 | 12346 | 426 | 82 | 534 | 22051 | 75235
LTC10289 | 1993-09-21 | 0 | 0 | 9 | 14 | 7 | 0 | 368 | 35591 | 80239
LTC10289 | 1993-10-26 | 0 | 0 | 0 | 0 | 0 | 28 | 281 | 32175 | 74220
LTC10289 | 1994-06-03 | 29 | 0 | 7 | 32 | 45 | 39 | 408 | 31354 | 70336
LTC10289 | 1994-07-07 | 23 | 0 | 0 | 11 | 23 | 23 | 325 | 33262 | 73305
LTC10289 | 1994-08-03 | 36 | 0 | 0 | 17 | 76 | 0 | 334 | 32894 | 71100
LTC10289 | 1995-08-21 | 28 | 6 | 0 | 22 | 93 | 77 | 393 | 31053 | 74571
LTC10289 | 1996-06-27 | 0 | 0 | 1 | 1 | 0 | 0 | 141 | 20213 | 44280
LTC10289 | 1996-06-27 | 39 | 0 | 0 | 6 | 42 | 0 | 207 | 21593 | 50060
LTC10289 | 2001-02-19 | 12 | 1 | 0 | 7 | 9 | 21 | 401 | 30302 | 69408
LTC10289 | 2002-03-04 | 18 | 2 | 0 | 11 | 41 | 50 | 415 | 26795 | 64248
LTC10289 | 2003-03-25 | 22 | 0 | 0 | 4 | 14 | 72 | 525 | 18715 | 68811
LTC10289 | 2004-02-23 | 21 | 0 | 0 | 5 | 31 | 34 | 386 | 24740 | 61319
LTC10289 | 2005-04-10 | 4 | 0 | 3 | 4 | 0 | 52 | 266 | 10485 | 51555
LTC10289 | 2005-05-24 | 20 | 0 | 0 | 6 | 28 | 0 | 305 | 30641 | 71720
LTC10290 | 1993-08-16 | 623 | 5450 | 1902 | 11833 | 374 | 414 | 1542 | 16399 | 70496
LTC10290 | 1993-08-26 | 510 | 4474 | 1575 | 8504 | 243 | 514 | 1833 | 15579 | 73725
LTC10290 | 1993-09-21 | 33 | 0 | 1 | 9 | 73 | 0 | 321 | 32759 | 75374
LTC10290 | 1993-11-08 | 17 | 0 | 12 | 10 | 43 | 0 | 360 | 35793 | 77509
LTC10290 | 1994-06-03 | 27 | 0 | 2 | 10 | 54 | 22 | 294 | 31718 | 69843
LTC10290 | 1994-07-07 | 17 | 0 | 0 | 13 | 61 | 0 | 299 | 34655 | 72680
LTC10290 | 1995-08-16 | 31 | 9 | 0 | 14 | 108 | 89 | 514 | 27692 | 75718
LTC10290 | 1996-04-11 | 15 | 0 | 0 | 10 | 40 | 52 | 450 | 29634 | 71245
LTC10290 | 1997-05-20 | 29 | 4 | 0 | 14 | 68 | 45 | 436 | 30356 | 71606
LTC10290 | 1998-06-11 | 23 | 0 | 2 | 9 | 55 | 39 | 400 | 25291 | 67130
LTC10290 | 2000-07-03 | 30 | 3 | 0 | 7 | 47 | 76 | 497 | 24859 | 74961
LTC10290 | 2001-06-18 | 14 | 3 | 0 | 8 | 23 | 28 | 344 | 27212 | 71459
LTC10290 | 2002-06-24 | 30 | 0 | 0 | 6 | 33 | 95 | 414 | 26746 | 70743
LTC10290 | 2003-08-07 | 31 | 0 | 0 | 9 | 45 | 69 | 415 | 26318 | 72193
LTC10290 | 2004-07-21 | 35 | 4 | 0 | 6 | 36 | 248 | 680 | 7376 | 72416
LTC10290 | 2005-03-23 | 10 | 6 | 0 | 6 | 0 | 34 | 1866 | 15879 | 71220
LTC10290 | 2005-04-03 | 286 | 56 | 10 | 137 | 388 | 63 | 930 | 20537 | 63032
LTC10290 | 2006-04-06 | 2 | 3 | 0 | 5 | 5 | 8 | 451 | 23603 | 61541
LTC10290 | 2006-05-26 | 12 | 2 | 0 | 3 | 14 | 14 | 417 | 25020 | 69457
LTC10294 | 1993-08-13 | 112 | 0 | 0 | 17 | 46 | 442 | 908 | 23075 | 69354
LTC10294 | 1994-05-26 | 77 | 0 | 0 | 8 | 35 | 119 | 611 | 23293 | 63134
LTC10294 | 1994-06-23 | 78 | 0 | 0 | 11 | 39 | 204 | 778 | 21340 | 66672
LTC10294 | 1994-07-26 | 70 | 0 | 2 | 8 | 48 | 220 | 916 | 20812 | 66394
LTC10294 | 1994-08-04 | 64 | 0 | 0 | 9 | 40 | 124 | 757 | 24534 | 69750
LTC10294 | 1995-08-16 | 23 | 3 | 0 | 14 | 55 | 21 | 403 | 30592 | 70030
LTC10294 | 1996-03-20 | 30 | 0 | 0 | 17 | 79 | 6 | 557 | 31096 | 64588
LTC10294 | 1997-05-27 | 13 | 0 | 0 | 12 | 43 | 0 | 416 | 30473 | 70639
LTC10294 | 1998-12-31 | 5 | 1 | 0 | 4 | 11 | 0 | 256 | 27421 | 66040
LTC10294 | 1999-11-16 | 12 | 0 | 0 | 4 | 15 | 0 | 310 | 28962 | 66896
LTC10294 | 2001-01-24 | 11 | 1 | 0 | 6 | 25 | 8 | 339 | 27654 | 62347
LTC10294 | 2001-12-05 | 4 | 3 | 7 | 4 | 0 | 7 | 415 | 24590 | 53933
LTC10294 | 2002-12-05 | 8 | 0 | 0 | 4 | 24 | 0 | 344 | 31851 | 70893
LTC10294 | 2003-12-17 | 9 | 4 | 0 | 6 | 25 | 31 | 407 | 22129 | 60850
LTC10294 | 2004-12-22 | 10 | 4 | 0 | 7 | 24 | 3 | 370 | 29054 | 63300
LTC10294 | 2006-05-23 | 458 | 166 | 21 | 308 | 1315 | 25 | 392 | 19992 | 56564
LTC10294 | 2006-05-30 | 22 | 5 | 1 | 14 | 27 | 29 | 458 | 19014 | 62922
LTC10300 | 1993-08-17 | 35 | 0 | 0 | 14 | 77 | 49 | 353 | 34471 | 78394
LTC10300 | 1994-05-25 | 68 | 0 | 0 | 14 | 97 | 55 | 354 | 29671 | 72955
LTC10300 | 1994-06-23 | 76 | 0 | 0 | 19 | 154 | 42 | 360 | 34244 | 78999
LTC10300 | 1994-07-26 | 61 | 0 | 0 | 19 | 186 | 15 | 388 | 33191 | 74892
LTC10300 | 1994-08-24 | 43 | 0 | 0 | 17 | 124 | 45 | 356 | 31724 | 73005
LTC10300 | 1995-08-10 | 19 | 3 | 0 | 16 | 68 | 63 | 450 | 30519 | 71766
LTC10300 | 1996-02-29 | 3 | 1 | 0 | 7 | 37 | 53 | 497 | 29249 | 68479
LTC10300 | 1997-05-21 | 28 | 0 | 0 | 8 | 49 | 69 | 517 | 27802 | 71181
LTC10300 | 1999-09-08 | 65 | 9 | 0 | 14 | 82 | 129 | 499 | 21107 | 70496
LTC10300 | 2000-09-12 | 33 | 6 | 0 | 10 | 59 | 8 | 416 | 25832 | 64570
LTC10300 | 2002-10-10 | 26 | 4 | 0 | 9 | 39 | 0 | 347 | 27314 | 66904
LTC10300 | 2003-09-24 | 26 | 5 | 2 | 8 | 37 | 50 | 365 | 27268 | 74314
LTC10300 | 2004-10-07 | 52 | 5 | 0 | 14 | 55 | 52 | 421 | 27141 | 71956
LTC10387 | 1993-09-22 | 78 | 0 | 3 | 6 | 33 | 68 | 674 | 28808 | 75388
LTC10387 | 1994-07-14 | 136 | 0 | 8 | 31 | 31 | 191 | 1085 | 17140 | 69817
LTC10387 | 1996-03-14 | 297 | 0 | 3 | 5 | 34 | 88 | 755 | 29810 | 75953
LTC10387 | 1997-05-19 | 72 | 4 | 0 | 5 | 33 | 85 | 871 | 22879 | 68667
LTC10387 | 1998-11-12 | 9 | 16 | 5 | 6 | 0 | 20 | 237 | 19428 | 68825
LTC10387 | 1999-10-06 | 5 | 0 | 0 | 2 | 15 | 0 | 394 | 28991 | 68400
LTC10387 | 2000-10-10 | 12 | 8 | 0 | 18 | 155 | 20 | 404 | 27645 | 68078
LTC10387 | 2001-11-28 | 0 | 0 | 0 | 1 | 1 | 15 | 348 | 23665 | 50698
LTC10387 | 2002-11-01 | 7 | 0 | 0 | 0 | 2 | 0 | 352 | 32442 | 73366
LTC10387 | 2003-10-02 | 3 | 0 | 0 | 0 | 0 | 15 | 458 | 31607 | 74787
LTC10387 | 2004-10-13 | 2 | 0 | 0 | 0 | 0 | 6 | 351 | 31966 | 72659
LTC10388 | 1993-09-22 | 88 | 0 | 0 | 6 | 41 | 85 | 705 | 27526 | 70833
LTC10388 | 1994-07-14 | 154 | 0 | 3 | 3 | 28 | 147 | 987 | 22419 | 72098
LTC10388 | 1996-03-08 | 43 | 0 | 0 | 0 | 24 | 48 | 569 | 26540 | 65848
LTC10388 | 1996-03-14 | 323 | 26 | 3 | 20 | 17 | 142 | 1015 | 29068 | 69339
LTC10388 | 1997-05-19 | 79 | 0 | 0 | 5 | 38 | 110 | 899 | 22083 | 67926
LTC10388 | 1998-11-12 | 7 | 13 | 7 | 2 | 0 | 27 | 290 | 19091 | 63510
LTC10388 | 1999-10-07 | 4 | 0 | 0 | 0 | 10 | 0 | 401 | 27157 | 65551
LTC10388 | 2000-10-10 | 6 | 5 | 0 | 10 | 81 | 0 | 368 | 29976 | 68112
LTC10388 | 2001-11-28 | 0 | 0 | 0 | 1 | 5 | 9 | 301 | 22102 | 47212
LTC10388 | 2002-11-01 | 3 | 0 | 0 | 2 | 3 | 0 | 323 | 31913 | 72497
LTC10388 | 2003-10-02 | 4 | 0 | 3 | 0 | 7 | 18 | 344 | 31537 | 75439
LTC10388 | 2004-10-13 | 3 | 0 | 0 | 0 | 0 | 6 | 372 | 33706 | 77020
LTC10430 | 1991-12-13 | 11 | 0 | 0 | 0 | 0 | 27 | 468 | 28507 | 71673
LTC10430 | 1993-09-27 | 23 | 0 | 6 | 32 | 0 | 85 | 597 | 25120 | 73257
LTC10430 | 1994-06-06 | 38 | 0 | 3 | 36 | 0 | 0 | 529 | 23545 | 70527
LTC10430 | 1996-04-23 | 37 | 0 | 1 | 1 | 0 | 52 | 539 | 25933 | 73190
LTC10430 | 1997-05-20 | 39 | 0 | 0 | 7 | 0 | 15 | 495 | 27487 | 65144
LTC10430 | 1997-12-30 | 32 | 45 | 10 | 70 | 0 | 33 | 525 | 24391 | 70648
LTC10430 | 1999-03-18 | 23 | 14 | 5 | 25 | 0 | 48 | 633 | 19760 | 69155
LTC10430 | 2000-01-31 | 7 | 0 | 0 | 0 | 0 | 12 | 411 | 26590 | 70781
LTC10430 | 2001-02-20 | 14 | 0 | 0 | 0 | 0 | 23 | 362 | 28056 | 68041
LTC10430 | 2002-02-20 | 35 | 0 | 0 | 0 | 0 | 48 | 474 | 25657 | 66432
LTC10430 | 2003-02-20 | 17 | 0 | 1 | 4 | 0 | 0 | 471 | 29145 | 66627
LTC10430 | 2004-02-03 | 12 | 0 | 0 | 0 | 0 | 20 | 396 | 28358 | 66559
LTC10430 | 2005-02-07 | 21 | 0 | 0 | 0 | 0 | 46 | 502 | 27343 | 75730
LTC10452 | 1993-09-23 | 0 | 0 | 0 | 0 | 0 | 377 | 445 | 32003 | 71973
LTC10452 | 1998-03-04 | 132 | 42 | 3 | 94 | 743 | 42 | 695 | 14716 | 72628
LTC10452 | 1999-06-08 | 1524 | 162 | 14 | 187 | 1476 | 208 | 676 | 15614 | 53169
LTC10452 | 2000-03-02 | 2435 | 353 | 18 | 362 | 2716 | 471 | 1070 | 11874 | 52023
LTC10488 | 1993-08-13 | 187 | 0 | 25 | 104 | 139 | 348 | 1106 | 17286 | 74891
LTC10488 | 1994-03-04 | 56 | 0 | 6 | 48 | 333 | 65 | 448 | 34721 | 80087
LTC10488 | 1994-05-26 | 142 | 0 | 0 | 7 | 44 | 214 | 776 | 20812 | 67765
LTC10488 | 1994-06-23 | 169 | 0 | 0 | 15 | 76 | 390 | 1300 | 14976 | 72938
LTC10488 | 1994-07-26 | 99 | 0 | 0 | 10 | 67 | 359 | 1149 | 16104 | 66491
LTC10488 | 1994-08-24 | 88 | 0 | 0 | 8 | 59 | 192 | 883 | 22075 | 67307
LTC10488 | 1995-08-14 | 198 | 10 | 0 | 21 | 135 | 212 | 929 | 24330 | 73620
LTC10488 | 1996-03-04 | 30 | 3 | 4 | 7 | 48 | 91 | 671 | 25412 | 64972
LTC10488 | 1997-05-21 | 11 | 0 | 1 | 12 | 68 | 0 | 450 | 33615 | 72430
LTC10488 | 1998-11-03 | 13 | 4 | 0 | 14 | 17 | 0 | 347 | 29738 | 70716
LTC10488 | 1999-10-26 | 15 | 3 | 0 | 15 | 75 | 0 | 347 | 28599 | 65303
LTC10488 | 2000-11-21 | 9 | 0 | 0 | 12 | 46 | 24 | 363 | 30798 | 74102
LTC10488 | 2001-10-24 | 21 | 10 | 1 | 33 | 123 | 28 | 436 | 13914 | 42782
LTC10488 | 2002-03-06 | 9 | 0 | 0 | 11 | 252 | 25 | 324 | 19354 | 50507
LTC10488 | 2002-12-18 | 22 | 4 | 1 | 24 | 81 | 0 | 392 | 31456 | 72177
LTC10488 | 2003-09-29 | 14 | 6 | 0 | 27 | 113 | 33 | 480 | 29455 | 71860
LTC10488 | 2003-10-23 | 18 | 3 | 2 | 16 | 72 | 38 | 468 | 29588 | 74565
LTC10488 | 2004-10-26 | 18 | 3 | 0 | 29 | 86 | 44 | 485 | 30086 | 75147
LTC10500 | 1993-09-23 | 0 | 0 | 0 | 3 | 0 | 23 | 404 | 32720 | 72550
LTC10500 | 1996-04-09 | 0 | 0 | 6 | 60 | 153 | 70 | 610 | 30994 | 71622
LTC10500 | 1996-12-16 | 2 | 0 | 0 | 20 | 0 | 70 | 680 | 27603 | 62907
LTC10500 | 1997-05-29 | 56 | 35 | 11 | 308 | 1890 | 70 | 690 | 30274 | 74140
LTC10500 | 1997-06-16 | 46 | 28 | 16 | 279 | 1612 | 66 | 698 | 29882 | 72779
LTC10500 | 1998-04-24 | 21 | 0 | 3 | 31 | 153 | 39 | 491 | 27036 | 71009
LTC10500 | 1999-04-12 | 22 | 13 | 16 | 55 | 148 | 34 | 708 | 28746 | 68207
LTC10500 | 2000-05-08 | 29 | 12 | 3 | 58 | 194 | 29 | 488 | 29264 | 68482
LTC10500 | 2001-10-11 | 38 | 24 | 5 | 76 | 441 | 25 | 453 | 29115 | 66609
LTC10500 | 2002-06-18 | 54 | 15 | 73 | 97 | 448 | 19 | 450 | 31378 | 70398
LTC10500 | 2003-06-16 | 16 | 11 | 78 | 65 | 220 | 29 | 407 | 29180 | 67299
LTC10500 | 2004-05-06 | 6 | 4 | 4 | 40 | 1 | 32 | 440 | 25643 | 63894
LTC10500 | 2005-06-22 | 7 | 0 | 3 | 16 | 53 | 23 | 406 | 31158 | 76306
LTC10501 | 1993-08-16 | 29 | 0 | 0 | 5 | 19 | 47 | 426 | 30521 | 77614
LTC10501 | 1994-06-07 | 15 | 0 | 0 | 5 | 21 | 42 | 348 | 29448 | 70558
LTC10501 | 1995-08-14 | 56 | 2 | 2 | 6 | 8 | 68 | 632 | 28630 | 74812
LTC10501 | 1995-10-04 | 14 | 2 | 0 | 12 | 35 | 9 | 374 | 39515 | 86809
LTC10501 | 1995-10-07 | 5 | 0 | 0 | 12 | 13 | 10 | 374 | 37093 | 72558
LTC10501 | 1996-06-03 | 0 | 0 | 1 | 0 | 0 | 0 | 210 | 28832 | 63186
LTC10501 | 1996-06-06 | 13 | 0 | 1 | 1 | 18 | 0 | 203 | 20588 | 45765
LTC10501 | 1997-05-23 | 29 | 7 | 6 | 13 | 125 | 0 | 421 | 31216 | 68386
LTC10501 | 1998-01-30 | 0 | 3 | 0 | 9 | 66 | 0 | 328 | 27204 | 61094
LTC10501 | 2000-07-03 | 6 | 0 | 0 | 0 | 3 | 12 | 319 | 27888 | 67767
LTC10501 | 2002-09-04 | 7 | 0 | 0 | 2 | 5 | 0 | 301 | 29562 | 67986
LTC10501 | 2003-08-04 | 9 | 0 | 0 | 0 | 8 | 12 | 312 | 30126 | 69552
LTC10501 | 2004-08-03 | 8 | 0 | 0 | 0 | 9 | 32 | 328 | 32457 | 77466
LTC10503 | 1993-09-02 | 145 | 0 | 0 | 11 | 89 | 103 | 630 | 25699 | 71226
LTC10503 | 1994-06-07 | 75 | 0 | 6 | 15 | 57 | 72 | 508 | 26620 | 70773
LTC10503 | 1995-08-10 | 73 | 5 | 0 | 14 | 77 | 75 | 561 | 27959 | 71534
LTC10503 | 1996-03-20 | 97 | 0 | 0 | 8 | 68 | 33 | 614 | 27814 | 67357
LTC10503 | 1997-05-27 | 54 | 4 | 2 | 11 | 30 | 46 | 633 | 24469 | 68580
LTC10503 | 1998-09-02 | 8 | 2 | 3 | 12 | 12 | 0 | 303 | 28292 | 69036
LTC10503 | 1999-08-15 | 7 | 0 | 0 | 0 | 0 | 0 | 399 | 27798 | 64177
LTC10503 | 2000-10-31 | 4 | 0 | 0 | 0 | 0 | 0 | 416 | 27470 | 62351
LTC10503 | 2001-10-24 | 5 | 5 | 0 | 8 | 25 | 27 | 349 | 12391 | 48136
LTC10503 | 2002-11-26 | 5 | 0 | 0 | 1 | 0 | 0 | 359 | 28370 | 66829
LTC10503 | 2003-12-01 | 8 | 0 | 0 | 4 | 19 | 36 | 397 | 24378 | 72746
LTC10503 | 2004-10-20 | 7 | 0 | 0 | 3 | 24 | 5 | 313 | 31064 | 69965
LTC10535 | 1993-08-16 | 38 | 0 | 6 | 5 | 26 | 119 | 623 | 23995 | 73463
LTC10535 | 1994-06-03 | 25 | 0 | 2 | 1 | 0 | 91 | 525 | 23986 | 70058
LTC10535 | 1994-07-07 | 21 | 0 | 3 | 2 | 0 | 88 | 573 | 20224 | 69817
LTC10535 | 1994-08-03 | 32 | 0 | 0 | 0 | 0 | 131 | 628 | 23852 | 68043
LTC10535 | 1995-08-16 | 99 | 2 | 0 | 11 | 45 | 212 | 913 | 23010 | 70364
LTC10535 | 1996-04-16 | 32 | 0 | 0 | 4 | 21 | 31 | 484 | 30279 | 69613
LTC10535 | 1996-04-19 | 43 | 0 | 0 | 7 | 36 | 38 | 499 | 29645 | 67421
LTC10535 | 1997-05-20 | 48 | 0 | 0 | 7 | 23 | 97 | 683 | 22567 | 72161
LTC10535 | 1998-07-07 | 88 | 3 | 0 | 4 | 22 | 206 | 890 | 10963 | 70578
LTC10535 | 1999-07-28 | 105 | 0 | 0 | 0 | 14 | 228 | 837 | 18465 | 64716
LTC10535 | 1999-10-07 | 8 | 0 | 0 | 0 | 0 | 0 | 292 | 24920 | 68188
LTC10535 | 2000-07-03 | 33 | 0 | 0 | 0 | 4 | 10 | 312 | 28144 | 70469
LTC10535 | 2002-01-29 | 0 | 0 | 0 | 0 | 8 | 0 | 282 | 23736 | 52772
LTC10535 | 2002-08-28 | 10 | 0 | 0 | 3 | 13 | 0 | 302 | 27849 | 66563
LTC10535 | 2003-08-07 | 7 | 0 | 0 | 0 | 14 | 0 | 305 | 28065 | 64609
LTC10535 | 2004-07-26 | 8 | 0 | 0 | 0 | 8 | 0 | 277 | 30441 | 70544
LTC10535 | 2005-07-25 | 26 | 0 | 0 | 2 | 12 | 40 | 390 | 22269 | 72522
LTC10541 | 1993-08-13 | 69 | 0 | 3 | 9 | 50 | 108 | 680 | 25034 | 68438
LTC10541 | 1994-05-26 | 69 | 0 | 0 | 8 | 37 | 200 | 657 | 26500 | 70760
LTC10541 | 1994-06-23 | 65 | 0 | 0 | 9 | 53 | 129 | 747 | 23400 | 67224
LTC10541 | 1994-07-26 | 57 | 0 | 3 | 9 | 60 | 135 | 700 | 25494 | 66554
LTC10541 | 1994-08-24 | 32 | 0 | 0 | 3 | 10 | 77 | 210 | 26687 | 73999
LTC10541 | 1995-08-10 | 62 | 3 | 0 | 6 | 47 | 151 | 823 | 25937 | 72068
LTC10541 | 1996-03-05 | 16 | 2 | 2 | 7 | 53 | 47 | 682 | 28672 | 67293
LTC10541 | 1997-05-21 | 48 | 5 | 1 | 8 | 42 | 67 | 642 | 27841 | 69027
LTC10541 | 1998-01-22 | 19 | 0 | 0 | 2 | 22 | 32 | 488 | 24776 | 66117
LTC10541 | 1999-02-25 | 22 | 6 | 0 | 4 | 36 | 0 | 450 | 30200 | 72064
LTC10541 | 2000-01-18 | 34 | 5 | 0 | 10 | 77 | 18 | 396 | 28841 | 66551
LTC10541 | 2003-11-21 | 17 | 3 | 0 | 6 | 36 | 6 | 341 | 31535 | 70307
LTC10541 | 2004-12-01 | 10 | 4 | 0 | 5 | 32 | 12 | 370 | 29482 | 65542
LTC10541 | 2005-08-01 | 13 | 0 | 0 | 8 | 36 | 13 | 363 | 31260 | 74890
LTC10544 | 1993-08-16 | 57 | 0 | 0 | 10 | 13 | 122 | 624 | 25473 | 69843
LTC10544 | 1994-06-03 | 14 | 0 | 0 | 2 | 4 | 87 | 515 | 22996 | 68380
LTC10544 | 1994-07-07 | 19 | 0 | 0 | 3 | 24 | 95 | 619 | 28819 | 73011
LTC10544 | 1994-08-03 | 28 | 0 | 0 | 0 | 18 | 203 | 552 | 26696 | 69615
LTC10544 | 1995-08-16 | 64 | 3 | 0 | 11 | 25 | 224 | 1050 | 21049 | 67505
LTC10544 | 1996-04-12 | 17 | 0 | 1 | 2 | 36 | 45 | 6885 | 27469 | 67418
LTC10544 | 1997-05-20 | 21 | 0 | 0 | 0 | 1 | 79 | 663 | 24447 | 69818
LTC10544 | 1998-07-07 | 45 | 0 | 0 | 3 | 16 | 118 | 718 | 19108 | 70497
LTC10544 | 1999-07-28 | 10 | 0 | 0 | 0 | 1 | 6 | 520 | 24732 | 60945
LTC10544 | 2000-07-03 | 6 | 0 | 0 | 0 | 0 | 10 | 379 | 28843 | 71886
LTC10544 | 2002-01-29 | 4 | 0 | 0 | 2 | 0 | 0 | 334 | 27305 | 62644
LTC10544 | 2002-08-28 | 6 | 0 | 0 | 2 | 11 | 11 | 290 | 28076 | 66740
LTC10544 | 2003-08-07 | 7 | 0 | 0 | 3 | 11 | 14 | 315 | 29003 | 68019
LTC10544 | 2004-07-26 | 4 | 0 | 0 | 0 | 0 | 2 | 265 | 30128 | 69742
LTC10544 | 2005-07-25 | 11 | 0 | 0 | 3 | 18 | 10 | 325 | 27697 | 69282
LTC10558 | 1993-09-30 | 20 | 0 | 1 | 14 | 41 | 0 | 455 | 34230 | 70650
LTC10558 | 1994-06-20 | 55 | 0 | 0 | 7 | 54 | 121 | 751 | 24411 | 72703
LTC10558 | 1996-03-25 | 117 | 9 | 0 | 8 | 80 | 50 | 568 | 31833 | 70543
LTC10558 | 1997-05-21 | 60 | 0 | 0 | 6 | 46 | 66 | 653 | 24775 | 71662
LTC10558 | 1998-12-09 | 6 | 1 | 3 | 0 | 7 | 0 | 325 | 26553 | 60239
LTC10558 | 1999-09-09 | 12 | 2 | 0 | 4 | 24 | 0 | 335 | 30701 | 70711
LTC10558 | 2000-09-20 | 11 | 0 | 0 | 7 | 13 | 0 | 355 | 27761 | 63852
LTC10558 | 2002-10-16 | 9 | 0 | 1 | 4 | 11 | 60 | 354 | 30673 | 70269
LTC10558 | 2003-09-23 | 10 | 0 | 1 | 2 | 2 | 0 | 297 | 29916 | 67930
LTC10558 | 2004-09-09 | 7 | 0 | 0 | 0 | 0 | 17 | 306 | 41545 | 96651
LTC10562 | 1993-08-13 | 93 | 0 | 0 | 8 | 68 | 91 | 723 | 24258 | 75620
LTC10562 | 1994-05-26 | 86 | 0 | 0 | 6 | 36 | 66 | 519 | 27282 | 68779
LTC10562 | 1994-06-23 | 68 | 0 | 3 | 8 | 43 | 82 | 675 | 26043 | 69369
LTC10562 | 1994-07-26 | 58 | 0 | 0 | 4 | 36 | 76 | 608 | 25124 | 64996
LTC10562 | 1994-08-24 | 47 | 0 | 0 | 4 | 42 | 40 | 566 | 27743 | 69289
LTC10562 | 1995-08-15 | 72 | 1 | 0 | 7 | 27 | 87 | 710 | 24671 | 68695
LTC10562 | 1996-03-04 | 27 | 0 | 4 | 2 | 12 | 36 | 611 | 28273 | 66749
LTC10562 | 1997-05-21 | 47 | 0 | 0 | 3 | 16 | 48 | 618 | 26204 | 67213
LTC10562 | 1998-03-16 | 10 | 0 | 0 | 0 | 0 | 5 | 417 | 29091 | 69716
LTC10562 | 1999-04-13 | 50 | 2 | 0 | 2 | 21 | 52 | 540 | 24752 | 71111
LTC10562 | 2000-03-31 | 47 | 0 | 0 | 4 | 36 | 40 | 493 | 26683 | 70682
LTC10562 | 2001-05-24 | 47 | 2 | 2 | 4 | 38 | 80 | 574 | 19719 | 66178
LTC10562 | 2002-05-17 | 77 | 22 | 10 | 4 | 29 | 90 | 681 | 24875 | 69914
LTC10562 | 2003-05-29 | 86 | 0 | 0 | 5 | 42 | 72 | 739 | 19849 | 68932
LTC10562 | 2004-05-05 | 19 | 4 | 6 | 26 | 36 | 4 | 403 | 29764 | 67535
LTC10562 | 2005-05-10 | 10 | 0 | 0 | 3 | 12 | 0 | 339 | 30309 | 68320
LTC10653 | 1993-09-27 | 27 | 0 | 0 | 0 | 0 | 32 | 449 | 25833 | 67605
LTC10653 | 1994-07-19 | 39 | 0 | 7 | 3 | 0 | 58 | 599 | 21868 | 70836
LTC10653 | 1996-03-14 | 264 | 33 | 12 | 42 | 259 | 40 | 610 | 19660 | 67502
LTC10653 | 1997-05-20 | 137 | 14 | 0 | 25 | 191 | 40 | 712 | 14027 | 69197
LTC10653 | 1998-02-04 | 103 | 19 | 11 | 28 | 202 | 19 | 451 | 26071 | 70261
LTC10653 | 1999-01-27 | 151 | 14 | 3 | 22 | 150 | 74 | 658 | 15238 | 62884
LTC10653 | 2000-02-28 | 16 | 2 | 0 | 6 | 37 | 0 | 338 | 29421 | 68568
LTC10653 | 2001-03-14 | 17 | 2 | 0 | 9 | 41 | 14 | 400 | 30323 | 69891
LTC10653 | 2002-01-22 | 16 | 3 | 0 | 19 | 52 | 22 | 380 | 31119 | 66444
LTC10653 | 2003-03-06 | 14 | 0 | 0 | 7 | 32 | 0 | 398 | 26507 | 62172
LTC10653 | 2004-02-19 | 15 | 0 | 0 | 5 | 22 | 24 | 445 | 28464 | 84697
LTC10653 | 2005-02-23 | 11 | 0 | 1 | 5 | 20 | 22 | 539 | 29361 | 68424
LTC10656 | 1993-08-17 | 66 | 0 | 4 | 16 | 74 | 88 | 648 | 25010 | 69304
LTC10656 | 1994-05-25 | 93 | 0 | 0 | 5 | 29 | 175 | 836 | 8163 | 67613
LTC10656 | 1994-06-23 | 64 | 0 | 5 | 15 | 58 | 100 | 560 | 30117 | 75098
LTC10656 | 1994-07-26 | 50 | 0 | 0 | 10 | 71 | 95 | 633 | 28607 | 70667
LTC10656 | 1994-08-24 | 44 | 0 | 0 | 10 | 62 | 62 | 522 | 28311 | 67726
LTC10656 | 1995-08-10 | 85 | 3 | 0 | 13 | 59 | 170 | 906 | 23571 | 67896
LTC10656 | 1996-02-29 | 26 | 1 | 0 | 6 | 30 | 88 | 683 | 22161 | 64336
LTC10656 | 1997-05-21 | 55 | 5 | 3 | 17 | 68 | 124 | 783 | 18421 | 66544
LTC10656 | 1998-08-24 | 120 | 7 | 1 | 9 | 50 | 208 | 939 | 15118 | 65422
LTC10656 | 2000-08-02 | 61 | 4 | 0 | 7 | 45 | 106 | 603 | 23090 | 68126
LTC10656 | 2002-10-04 | 82 | 6 | 2 | 11 | 49 | 186 | 868 | 18044 | 63723
LTC10656 | 2003-09-02 | 131 | 0 | 0 | 13 | 86 | 235 | 802 | 20889 | 71787
LTC10656 | 2003-12-16 | 28 | 0 | 0 | 8 | 57 | 39 | 430 | 24961 | 69221
LTC10660 | 1997-05-20 | 36 | 0 | 0 | 20 | 75 | 0 | 353 | 31889 | 69770
LTC10660 | 1998-04-01 | 20 | 1 | 0 | 8 | 40 | 0 | 308 | 27252 | 65192
LTC10660 | 1999-05-27 | 12 | 3 | 0 | 6 | 28 | 0 | 374 | 27066 | 68062
LTC10660 | 2000-04-13 | 11 | 0 | 0 | 0 | 3 | 19 | 297 | 28887 | 71216
LTC10660 | 2001-05-03 | 21 | 0 | 0 | 6 | 32 | 19 | 344 | 27967 | 68967
LTC10660 | 2002-03-20 | 16 | 2 | 0 | 4 | 21 | 26 | 446 | 25910 | 68195
LTC10660 | 2002-05-02 | 21 | 2 | 0 | 6 | 32 | 26 | 332 | 25946 | 67512
LTC10660 | 2003-05-14 | 15 | 1 | 0 | 4 | 1 | 48 | 368 | 25586 | 67669
LTC10660 | 2004-04-15 | 168 | 21 | 4 | 69 | 460 | 102 | 481 | 24088 | 69116
LTC10660 | 2005-03-03 | 4 | 2 | 0 | 0 | 0 | 10 | 312 | 28517 | 66538
LTC10660 | 2006-04-04 | 2 | 10 | 18 | 62 | 5 | 10 | 341 | 20765 | 55377
LTC10662 | 1993-08-16 | 81 | 0 | 7 | 42 | 82 | 165 | 757 | 23222 | 70868
LTC10662 | 1994-06-03 | 42 | 0 | 2 | 9 | 43 | 88 | 452 | 27830 | 67614
LTC10662 | 1994-07-07 | 42 | 0 | 0 | 13 | 84 | 101 | 686 | 29269 | 72434
LTC10662 | 1994-08-03 | 125 | 0 | 15 | 19 | 151 | 124 | 726 | 26934 | 70021
LTC10662 | 1995-08-21 | 92 | 8 | 0 | 12 | 95 | 249 | 1140 | 22470 | 69858
LTC10662 | 1996-04-11 | 116 | 0 | 0 | 11 | 70 | 54 | 592 | 28241 | 72110
LTC10662 | 1997-05-20 | 79 | 0 | 0 | 8 | 67 | 124 | 763 | 24603 | 68120
LTC10662 | 1998-06-11 | 85 | 5 | 2 | 10 | 52 | 179 | 859 | 13810 | 65469
LTC10662 | 1999-07-06 | 91 | 3 | 0 | 7 | 45 | 23 | 772 | 20760 | 71502
LTC10662 | 2000-07-03 | 86 | 3 | 0 | 6 | 40 | 223 | 834 | 19238 | 73250
LTC10662 | 2001-06-18 | 69 | 2 | 0 | 7 | 29 | 141 | 688 | 21246 | 73082
LTC10662 | 2002-06-24 | 18 | 0 | 0 | 0 | 6 | 2 | 349 | 20342 | 68157
LTC10662 | 2003-08-07 | 123 | 0 | 0 | 0 | 9 | 55 | 556 | 16187 | 67908
LTC10662 | 2004-10-29 | 5 | 2 | 1 | 1 | 0 | 12 | 488 | 11018 | 80537
LTC10662 | 2005-05-26 | 8 | 0 | 0 | 2 | 9 | 14 | 337 | 25275 | 71636
LTC10663 | 1993-08-16 | 129 | 0 | 3 | 6 | 40 | 211 | 876 | 21476 | 73589
LTC10663 | 1994-06-07 | 52 | 0 | 0 | 5 | 35 | 86 | 465 | 29373 | 69944
LTC10663 | 1995-08-16 | 128 | 0 | 0 | 6 | 46 | 213 | 1008 | 19244 | 69394
LTC10663 | 1996-04-11 | 35 | 0 | 3 | 4 | 26 | 29 | 535 | 30462 | 72858
LTC10663 | 1997-05-20 | 75 | 4 | 3 | 31 | 29 | 179 | 872 | 15600 | 68371
LTC10663 | 1998-06-11 | 78 | 4 | 0 | 8 | 41 | 171 | 834 | 16716 | 66637
LTC10663 | 1999-07-07 | 8 | 0 | 1 | 0 | 1 | 0 | 302 | 29813 | 72394
LTC10663 | 2000-07-03 | 5 | 0 | 0 | 0 | 0 | 17 | 394 | 26907 | 72176
LTC10663 | 2001-06-18 | 6 | 0 | 0 | 0 | 0 | 0 | 416 | 28748 | 67313
LTC10663 | 2002-06-24 | 13 | 0 | 0 | 0 | 4 | 0 | 290 | 30221 | 70941
LTC10663 | 2005-04-21 | 5 | 0 | 2 | 6 | 0 | 52 | 264 | 8508 | 47670
LTC10663 | 2005-06-17 | 0 | 0 | 0 | 3 | 0 | 24 | 353 | 26304 | 69366
LTC10669 | 1993-09-03 | 116 | 0 | 0 | 13 | 95 | 169 | 768 | 25864 | 76864
LTC10669 | 1994-05-13 | 57 | 0 | 0 | 5 | 30 | 80 | 570 | 27148 | 69307
LTC10669 | 1996-03-26 | 24 | 258 | 75 | 274 | 16 | 175 | 806 | 19490 | 66945
LTC10669 | 1996-06-07 | 42 | 0 | 3 | 20 | 51 | 112 | 614 | 26725 | 70014
LTC10669 | 1997-07-09 | 128 | 126 | 40 | 293 | 72 | 325 | 870 | 18388 | 68579
LTC10669 | 1998-11-20 | 39 | 5 | 7 | 4 | 29 | 53 | 552 | 20748 | 60691
LTC10669 | 1999-09-08 | 125 | 3 | 0 | 6 | 29 | 286 | 1108 | 9012 | 67639
LTC10669 | 2000-09-15 | 56 | 0 | 0 | 0 | 5 | 78 | 713 | 16296 | 62629
LTC10669 | 2001-11-05 | 37 | 1 | 0 | 2 | 7 | 95 | 841 | 13326 | 51069
LTC10669 | 2002-10-16 | 20 | 0 | 0 | 2 | 10 | 55 | 478 | 27225 | 67327
LTC10669 | 2003-09-23 | 17 | 0 | 0 | 1 | 1 | 43 | 436 | 26212 | 64305
LTC10669 | 2004-08-26 | 42 | 0 | 0 | 1 | 0 | 45 | 486 | 26939 | 67910
LTC10669 | 2005-10-05 | 5 | 1 | 0 | 2 | 47 | 18 | 687 | 613 | 1222
LTC11028 | 1993-08-17 | 127 | 0 | 0 | 9 | 6 | 119 | 750 | 20004 | 68489
LTC11625 | 1993-09-07 | 52 | 0 | 6 | 57 | 259 | 45 | 594 | 32096 | 70610
LTC11625 | 1993-10-12 | 80 | 0 | 5 | 58 | 269 | 84 | 609 | 30543 | 74066
LTC11625 | 1994-06-14 | 29 | 0 | 0 | 32 | 151 | 63 | 617 | 31307 | 75002
LTC11625 | 1996-04-08 | 36 | 6 | 2 | 29 | 130 | 51 | 641 | 27708 | 68358
LTC11625 | 1997-05-29 | 28 | 4 | 0 | 25 | 148 | 51 | 674 | 32108 | 75232
LTC11625 | 1998-09-01 | 28 | 10 | 26 | 28 | 129 | 0 | 471 | 29105 | 66361
LTC11625 | 1999-09-08 | 24 | 11 | 4 | 49 | 158 | 18 | 448 | 28539 | 66939
LTC11625 | 2000-08-28 | 46 | 11 | 4 | 49 | 179 | 0 | 460 | 28559 | 64125
LTC11625 | 2001-11-01 | 47 | 52 | 26 | 216 | 553 | 67 | 634 | 11136 | 38833
LTC11625 | 2002-10-10 | 4 | 3 | 4 | 29 | 13 | 0 | 489 | 32251 | 71815
LTC11625 | 2003-09-16 | 62 | 8 | 4 | 41 | 120 | 28 | 505 | 27777 | 68422
LTC11625 | 2004-09-21 | 134 | 41 | 8 | 138 | 793 | 21 | 514 | 31677 | 74161
LTC11625 | 2005-01-05 | 136 | 59 | 12 | 222 | 1328 | 141 | 566 | 30543 | 67185
LTC11628 | 1993-09-10 | 27 | 0 | 0 | 10 | 57 | 77 | 497 | 27868 | 69985
LTC11628 | 1994-06-10 | 17 | 0 | 0 | 4 | 17 | 152 | 818 | 7817 | 74307
LTC11628 | 1996-04-23 | 7 | 0 | 0 | 3 | 11 | 29 | 409 | 28120 | 70710
LTC11628 | 1997-05-16 | 20 | 2 | 0 | 3 | 0 | 62 | 634 | 18459 | 67931
LTC11628 | 1998-08-31 | 17 | 3 | 0 | 0 | 21 | 71 | 488 | 18489 | 57666
LTC11628 | 1999-09-13 | 15 | 2 | 0 | 2 | 14 | 68 | 492 | 22846 | 68844
LTC11628 | 2000-10-10 | 17 | 0 | 0 | 4 | 16 | 84 | 519 | 16649 | 68687
LTC11628 | 2001-10-10 | 8 | 6 | 0 | 8 | 12 | 18 | 485 | 20432 | 65859
LTC11628 | 2002-11-01 | 6 | 4 | 0 | 2 | 2 | 66 | 407 | 29731 | 71507
LTC11628 | 2003-09-29 | 3 | 3 | 0 | 0 | 0 | 8 | 305 | 29100 | 67212
LTC11628 | 2004-09-22 | 0 | 0 | 0 | 0 | 0 | 12 | 345 | 28701 | 66990
LTC11629 | 1993-09-10 | 45 | 0 | 7 | 45 | 2239 | 184 | 1781 | 14200 | 78221
LTC11629 | 1994-06-10 | 37 | 0 | 13 | 36 | 181 | 68 | 1064 | 21663 | 74046
LTC11629 | 1996-04-23 | 42 | 11 | 6 | 38 | 200 | 151 | 1119 | 17553 | 67608
LTC11629 | 1998-08-31 | 74 | 23 | 2 | 28 | 158 | 189 | 1580 | 20234 | 68238
LTC11629 | 1999-09-13 | 56 | 12 | 0 | 30 | 271 | 174 | 1647 | 18681 | 67067
LTC11629 | 2000-10-10 | 1466 | 17070 | 12552 | 42577 | 630 | 289 | 2613 | 7759 | 61623
LTC11629 | 2001-10-10 | 19 | 26 | 17 | 110 | 359 | 30 | 850 | 18305 | 56328
LTC11629 | 2002-11-01 | 50 | 12 | 6 | 44 | 194 | 0 | 596 | 29710 | 71251
LTC11629 | 2003-09-29 | 26 | 8 | 4 | 40 | 161 | 26 | 588 | 29339 | 67811
LTC11629 | 2004-09-22 | 22 | 9 | 2 | 36 | 146 | 20 | 559 | 27172 | 62905
LTC11630 | 1993-09-27 | 30 | 0 | 0 | 7 | 25 | 0 | 415 | 33713 | 73626
LTC11630 | 1994-06-06 | 22 | 0 | 0 | 4 | 45 | 50 | 368 | 31896 | 72261
LTC11630 | 1996-04-23 | 29 | 0 | 0 | 6 | 35 | 102 | 514 | 28758 | 73742
LTC11630 | 1997-05-20 | 17 | 0 | 0 | 8 | 39 | 23 | 489 | 29454 | 64587
LTC11630 | 1998-04-28 | 12 | 0 | 0 | 5 | 27 | 41 | 371 | 32630 | 77415
LTC11630 | 1999-05-26 | 15 | 2 | 0 | 4 | 30 | 37 | 424 | 27928 | 71596
LTC11630 | 2000-04-28 | 6 | 0 | 0 | 0 | 8 | 7 | 362 | 29939 | 66451
LTC11630 | 2001-06-21 | 5 | 0 | 0 | 2 | 6 | 32 | 389 | 28848 | 69542
LTC11630 | 2002-07-19 | 5 | 0 | 2 | 0 | 8 | 9 | 323 | 28901 | 67308
LTC11630 | 2003-07-09 | 6 | 0 | 0 | 3 | 22 | 17 | 357 | 27516 | 65444
LTC11630 | 2004-06-22 | 5 | 0 | 0 | 0 | 8 | 0 | 450 | 28963 | 68169
LTC11630 | 2005-06-27 | 0 | 0 | 0 | 0 | 4 | 0 | 390 | 32732 | 70330
LTC11631 | 1993-09-27 | 19 | 0 | 1 | 11 | 47 | 38 | 364 | 33781 | 74834
LTC11631 | 1994-06-06 | 17 | 0 | 0 | 7 | 45 | 68 | 371 | 28962 | 74051
LTC11631 | 1996-04-23 | 40 | 0 | 2 | 8 | 50 | 50 | 628 | 32325 | 72040
LTC11631 | 1997-05-20 | 19 | 0 | 0 | 7 | 47 | 0 | 410 | 33698 | 70272
LTC11631 | 1998-04-28 | 11 | 0 | 0 | 0 | 26 | 35 | 422 | 30375 | 71594
LTC11631 | 1999-06-22 | 17 | 0 | 0 | 5 | 24 | 80 | 610 | 29126 | 78183
LTC11631 | 2000-05-30 | 4 | 0 | 0 | 0 | 0 | 14 | 394 | 27793 | 65725
LTC11631 | 2002-09-05 | 5 | 0 | 0 | 1 | 8 | 28 | 401 | 28017 | 70144
LTC11631 | 2003-07-09 | 3 | 0 | 0 | 2 | 6 | 11 | 340 | 29928 | 69530
LTC11631 | 2004-06-22 | 5 | 0 | 0 | 0 | 4 | 6 | 374 | 28824 | 69464
LTC11631 | 2005-06-26 | 7 | 0 | 0 | 2 | 8 | 0 | 300 | 29802 | 66496
LTC11820 | 1993-08-13 | 11 | 0 | 0 | 9 | 58 | 32 | 407 | 32389 | 74473
LTC11820 | 1994-06-07 | 18 | 0 | 0 | 8 | 49 | 33 | 333 | 32702 | 68003
LTC11820 | 1995-08-16 | 19 | 2 | 0 | 8 | 48 | 42 | 416 | 32791 | 70314
LTC11820 | 1996-03-20 | 21 | 1 | 0 | 5 | 38 | 29 | 604 | 32212 | 69444
LTC11820 | 1997-05-27 | 16 | 4 | 4 | 29 | 44 | 17 | 513 | 31336 | 70615
LTC11820 | 1998-03-27 | 10 | 0 | 0 | 4 | 37 | 28 | 391 | 26165 | 65050
LTC11820 | 1999-07-22 | 7 | 0 | 0 | 0 | 14 | 7 | 295 | 28219 | 69712
LTC11820 | 2000-04-19 | 6 | 0 | 0 | 3 | 6 | 49 | 382 | 23727 | 69418
LTC11820 | 2001-10-10 | 3 | 6 | 0 | 6 | 5 | 17 | 564 | 51012 | 277817
LTC11820 | 2002-05-14 | 5 | 0 | 0 | 4 | 14 | 34 | 378 | 29978 | 73848
LTC11820 | 2003-09-12 | 5 | 0 | 1 | 6 | 20 | 20 | 448 | 29158 | 69304
LTC11820 | 2004-07-27 | 10 | 1 | 0 | 5 | 22 | 25 | 333 | 28409 | 66886
LTC11820 | 2005-05-11 | 6 | 0 | 0 | 4 | 12 | 15 | 328 | 29242 | 68153
LTC11822 | 1993-09-27 | 20 | 0 | 0 | 12 | 86 | 41 | 396 | 33886 | 71525
LTC11822 | 1994-06-06 | 19 | 0 | 0 | 6 | 32 | 39 | 326 | 32143 | 77836
LTC11822 | 1996-05-01 | 31 | 0 | 1 | 9 | 45 | 67 | 469 | 28374 | 67346
LTC11822 | 1997-05-20 | 25 | 0 | 0 | 5 | 43 | 16 | 468 | 31530 | 72347
LTC11822 | 1998-02-10 | 23 | 2 | 0 | 6 | 73 | 52 | 489 | 28677 | 72278
LTC11822 | 1999-03-18 | 31 | 2 | 0 | 5 | 43 | 120 | 509 | 23242 | 71204
LTC11822 | 2000-03-14 | 5 | 0 | 0 | 0 | 8 | 0 | 347 | 28057 | 62625
LTC11822 | 2001-04-17 | 9 | 0 | 0 | 1 | 21 | 8 | 330 | 30498 | 68288
LTC11822 | 2003-02-18 | 5 | 0 | 0 | 3 | 7 | 0 | 389 | 28498 | 65212
LTC11822 | 2004-01-28 | 5 | 0 | 0 | 2 | 1 | 29 | 385 | 25869 | 62648
LTC11822 | 2005-02-04 | 6 | 0 | 0 | 0 | 0 | 20 | 442 | 29694 | 65144
LTC11833 | 1993-09-13 | 18 | 0 | 0 | 7 | 37 | 74 | 460 | 28422 | 69582
LTC11833 | 1996-04-03 | 14 | 0 | 1 | 2 | 12 | 40 | 479 | 30305 | 67350
LTC11833 | 1997-06-03 | 16 | 0 | 2 | 13 | 39 | 65 | 540 | 26937 | 67434
LTC11833 | 1998-10-23 | 12 | 2 | 0 | 4 | 19 | 33 | 379 | 22496 | 59540
LTC11833 | 2000-12-07 | 17 | 0 | 0 | 2 | 24 | 40 | 520 | 23852 | 62661
LTC11833 | 2001-11-21 | 18 | 4 | 0 | 2 | 12 | 60 | 479 | 17305 | 51629
LTC11833 | 2002-12-03 | 17 | 0 | 0 | 2 | 18 | 0 | 522 | 22654 | 69650
LTC11833 | 2004-12-01 | 17 | 3 | 0 | 5 | 23 | 74 | 649 | 22813 | 69652
LTC11847 | 1993-09-02 | 48 | 0 | 6 | 12 | 52 | 45 | 343 | 32583 | 70683
LTC11847 | 1994-06-07 | 36 | 0 | 0 | 6 | 43 | 32 | 325 | 31453 | 66253
LTC11847 | 1995-08-16 | 38 | 5 | 0 | 18 | 104 | 39 | 421 | 31513 | 70384
LTC11847 | 1996-03-20 | 26 | 0 | 8 | 20 | 51 | 20 | 569 | 34677 | 68993
LTC11847 | 1997-02-26 | 0 | 0 | 0 | 0 | 0 | 0 | 268 | 23798 | 51034
LTC11847 | 1997-03-03 | 30 | 0 | 0 | 3 | 11 | 0 | 324 | 28326 | 59216
LTC11889 | 1993-08-13 | 41 | 0 | 0 | 11 | 56 | 31 | 412 | 34092 | 77150
LTC11889 | 1994-06-07 | 23 | 0 | 0 | 15 | 43 |  | 316 | 28296 | 66106
LTC11889 | 1995-08-16 | 30 | 2 | 0 | 6 | 58 | 37 | 407 | 32033 | 73067
LTC11889 | 1996-03-20 | 40 | 3 | 0 | 11 | 56 | 15 | 451 | 33876 | 70400
LTC11889 | 1997-05-23 | 21 | 2 | 0 | 4 | 50 | 0 | 417 | 33236 | 71036
LTC11889 | 1998-01-09 | 15 | 0 | 0 | 13 | 50 | 66 | 376 | 39590 | 78725
LTC11889 | 1999-03-19 | 15 | 4 | 3 | 4 | 34 | 81 | 492 | 24263 | 71027
LTC11889 | 2000-06-29 | 6 | 0 | 0 | 0 | 6 | 0 | 295 | 29874 | 69327
LTC11889 | 2001-04-03 | 5 | 0 | 1 | 4 | 13 | 10 | 352 | 29152 | 64493
LTC11889 | 2002-09-17 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 25935 | 66650
LTC11889 | 2003-04-02 | 8 | 0 | 0 | 4 | 12 | 0 | 370 | 28870 | 65062
LTC11889 | 2004-03-11 | 7 | 0 | 0 | 3 | 8 | 20 | 385 | 26840 | 61248
LTC11889 | 2006-03-22 | 7 | 5 | 0 | 7 | 7 | 40 | 552 | 20057 | 57018
LTC11889 | 2006-04-13 | 1 | 4 | 1 | 23 | 1 | 7 | 515 | 24405 | 62021
LTC11920 | 1993-09-13 | 59 | 0 | 0 | 14 | 66 | 47 | 539 | 26834 | 66295
LTC11920 | 1994-06-01 | 67 | 0 | 0 | 6 | 45 | 46 | 453 | 28194 | 72023
LTC11920 | 1996-04-03 | 261 | 0 | 3 | 6 | 45 | 78 | 723 | 17163 | 64716
LTC11920 | 1997-06-03 | 86 | 0 | 3 | 3 | 30 | 166 | 886 | 11825 | 67227
LTC11920 | 1998-10-23 | 80 | 5 | 1 | 7 | 49 | 165 | 913 | 6751 | 65213
LTC11920 | 1999-12-16 | 56 | 3 | 0 | 5 | 31 | 120 | 831 | 7674 | 73271
LTC11920 | 2000-12-07 | 102 | 2 | 0 | 5 | 40 | 62 | 690 | 21331 | 63458
LTC11920 | 2001-11-21 | 65 | 2 | 0 | 3 | 20 | 84 | 643 | 16130 | 53892
LTC11920 | 2002-12-13 | 44 | 0 | 0 | 3 | 25 | 51 | 564 | 23399 | 65353
LTC11920 | 2003-11-13 | 59 | 5 | 0 | 13 | 36 | 119 | 705 | 19728 | 75266
LTC11920 | 2004-12-01 | 33 | 2 | 0 | 3 | 28 | 36 | 514 | 28390 | 71599
LTC12000 | 1993-09-03 | 193 | 0 | 2 | 42 | 180 | 80 | 392 | 34607 | 72706
LTC12000 | 1994-05-13 | 33 | 0 | 0 | 12 | 58 | 125 | 540 | 25312 | 70254
LTC12000 | 1996-04-03 | 25 | 0 | 0 | 12 | 63 | 29 | 466 | 33505 | 71004
LTC12000 | 1997-06-10 | 40 | 2 | 2 | 13 | 66 | 140 | 524 | 27237 | 68998
LTC12000 | 1998-07-23 | 66 | 9 | 3 | 17 | 90 | 288 | 677 | 15933 | 76734
LTC12000 | 1999-07-16 | 47 | 4 | 0 | 7 | 0 | 179 | 642 | 15889 | 65472
LTC12000 | 2000-05-11 | 54 | 5 | 0 | 9 | 62 | 227 | 753 | 6803 | 66213
LTC12000 | 2002-06-26 | 163 | 6 | 2 | 11 | 81 | 209 | 966 | 16040 | 72367
LTC12000 | 2003-06-26 | 176 | 2 | 1 | 6 | 36 | 259 | 916 | 11025 | 63977
LTC12000 | 2004-02-25 | 16 | 0 | 0 | 3 | 1 | 40 | 444 | 29283 | 67815
LTC12000 | 2005-07-25 | 56 | 0 | 0 | 4 | 28 | 293 | 1075 | 11240 | 71155
LTC12001 | 1993-09-03 | 232 | 0 | 8 | 39 | 151 | 48 | 402 | 35486 | 73831
LTC12001 | 1994-05-13 | 23 | 0 | 2 | 8 | 31 | 104 | 556 | 25296 | 68971
LTC12001 | 1996-04-03 | 34 | 0 | 3 | 9 | 44 | 33 | 538 | 34191 | 71183
LTC12001 | 1997-06-10 | 29 | 1 | 0 | 10 | 34 | 88 | 452 | 30733 | 68240
LTC12001 | 1998-07-23 | 50 | 8 | 0 | 13 | 60 | 201 | 553 | 22258 | 79150
LTC12001 | 1999-07-16 | 41 | 3 | 0 | 7 | 0 | 203 | 635 | 15268 | 66146
LTC12001 | 2000-05-11 | 51 | 5 | 0 | 7 | 58 | 97 | 485 | 20391 | 65888
LTC12001 | 2002-06-26 | 142 | 5 | 1 | 10 | 52 | 253 | 954 | 9318 | 73210
LTC12001 | 2003-06-26 | 90 | 0 | 0 | 3 | 30 | 151 | 723 | 19730 | 63883
LTC12001 | 2004-03-12 | 36 | 0 | 0 | 3 | 20 | 70 | 489 | 24360 | 63982
LTC12001 | 2004-07-13 | 57 | 0 | 0 | 0 | 0 | 166 | 789 | 20126 | 67305

## Data
IEEE Std C57.139-2010 Guide for Dissolved Gas Analysis in Transformer Load Tap Changers Statistics Calculator
|  | Individual LTC Model: | Enter the LTC model here
|  | Breathing Type: | Enter the description of the breathing type here |  |  |  |  | Compartment: | Enter compartment designation, if applicable
|  |  | Contact Type | Bridging Impedance | Compartments | Tank
|  | Generic LTC Type: | A | R | A | S
Arcing Contacts; Resistor Type; One compartment: arcing type selector; Sealed Tank: with/without pressure relief
|  |  | 0 | 0 | 0
All concentractions herein are in units of μL/L
| Minimum Reliable Value --> | 10 | 10 | 10 | 10 | 10 |  |  |  |  | 12.5
0 |  | H2 | CH4 | C2H6 | C2H4 | C2H2 | CO | CO2 | O2 | N2 | Methane + Ethane + Ethylene
Equipment ID | Sample Date | Hydrogen | Methane | Ethane | Ethylene | Acetylene | Carbon Monoxide | Carbon Dioxide | Oxygen | Nitrogen | TDHG
LTC04773 | 1997-07-24 | 20 | 0 | 0 | 4 | 38 | 76 | 501 | 25244 | 68031 | 4
LTC04773 | 1998-04-16 | 12 | 1 | 7 | 5 | 19 | 35 | 416 | 25583 | 67848 | 13
LTC04773 | 1999-07-19 | 16 | 2 | 0 | 3 | 25 | 191 | 546 | 9406 | 67332 | 5
LTC04773 | 2000-05-25 | 14 | 0 | 0 | 0 | 17 | 48 | 363 | 26015 | 69090 | 0
LTC04773 | 2001-06-19 | 25 | 2 | 0 | 0 | 20 | 46 | 424 | 21726 | 70109 | 2
LTC04773 | 2002-11-25 | 11 | 0 | 0 | 0 | 24 | 80 | 425 | 24276 | 66590 | 0
LTC04773 | 2003-06-26 | 21 | 0 | 0 | 11 | 29 | 106 | 501 | 22104 | 68343 | 11
LTC04774 | 1993-09-14 | 20 | 0 | 0 | 0 | 10 | 38 | 379 | 35156 | 70731 | 0
LTC04774 | 1994-06-01 | 7 | 0 | 5 | 2 | 0 | 23 | 383 | 28697 | 66399 | 7
LTC04774 | 1997-07-24 | 7 | 2 | 0 | 0 | 0 | 71 | 496 | 24780 | 67573 | 2
LTC04774 | 1998-04-16 | 7 | 0 | 0 | 0 | 0 | 0 | 391 | 28665 | 67359 | 0
LTC04774 | 1999-07-19 | 4 | 0 | 0 | 0 | 0 | 34 | 366 | 21866 | 67243 | 0
LTC04774 | 2000-05-25 | 4 | 0 | 1 | 1 | 0 | 11 | 388 | 30483 | 70206 | 2
LTC04774 | 2001-06-19 | 0 | 0 | 0 | 0 | 0 | 0 | 443 | 26134 | 67575 | 0
LTC04774 | 2003-06-26 | 3 | 0 | 0 | 0 | 0 | 28 | 402 | 27916 | 69855 | 0
LTC04774 | 2004-06-23 | 4 | 0 | 0 | 0 | 0 | 43 | 448 | 16511 | 65369 | 0
LTC04775 | 1993-09-14 | 36 | 0 | 15 | 74 | 40 | 43 | 472 | 28538 | 70171 | 89
LTC04775 | 1994-06-01 | 15 | 0 | 0 | 3 | 23 | 91 | 540 | 18280 | 76351 | 3
LTC04775 | 1997-07-24 | 19 | 0 | 0 | 6 | 57 | 76 | 505 | 27588 | 73766 | 6
LTC04775 | 1998-04-16 | 9 | 0 | 0 | 7 | 19 | 0 | 391 | 28737 | 67354 | 7
LTC04775 | 1999-07-19 | 21 | 1 | 0 | 3 | 26 | 150 | 518 | 13493 | 66247 | 4
LTC04775 | 2000-05-25 | 15 | 0 | 0 | 1 | 21 | 40 | 429 | 26193 | 65329 | 1
LTC04775 | 2001-06-19 | 21 | 1 | 0 | 4 | 25 | 80 | 463 | 17321 | 69896 | 5
LTC04775 | 2002-11-25 | 16 | 0 | 0 | 3 | 26 | 32 | 459 | 23731 | 66437 | 3
LTC04775 | 2003-06-26 | 18 | 0 | 0 | 5 | 30 | 87 | 519 | 24046 | 68696 | 5
LTC04775 | 2004-06-23 | 32 | 0 | 0 | 4 | 32 | 276 | 675 | 9590 | 71832 | 4
LTC04776 | 1993-09-14 | 34 | 0 | 0 | 4 | 42 | 20 | 368 | 33329 | 68537 | 4
LTC04776 | 1994-06-01 | 17 | 0 | 0 | 3 | 17 | 37 | 387 | 27033 | 68296 | 3
LTC04776 | 1998-04-16 | 11 | 0 | 0 | 4 | 18 | 0 | 422 | 28833 | 67609 | 4
LTC04776 | 1999-07-19 | 3 | 2 | 0 | 4 | 30 | 146 | 599 | 14536 | 66412 | 6
LTC04776 | 2000-05-25 | 48 | 0 | 0 | 4 | 18 | 58 | 408 | 24495 | 68456 | 4
LTC04776 | 2001-06-19 | 79 | 1 | 0 | 2 | 42 | 15 | 418 | 26146 | 67317 | 3
LTC04776 | 2003-06-26 | 20 | 0 | 0 | 5 | 36 | 90 | 437 | 23800 | 70370 | 5
LTC04776 | 2004-06-23 | 37 | 0 | 0 | 4 | 26 | 247 | 731 | 6736 | 65635 | 4
LTC06962 | 1993-09-08 | 14 | 0 | 0 | 2 | 14 | 64 | 541 | 26632 | 67683 | 2
LTC06962 | 1994-06-01 | 15 | 0 | 0 | 0 | 10 | 40 | 375 | 30952 | 68792 | 0
LTC06962 | 1998-10-28 | 16 | 0 | 0 | 1 | 9 | 3 | 459 | 24897 | 65234 | 1
LTC06962 | 1999-10-13 | 19 | 0 | 0 | 0 | 9 | 15 | 452 | 24904 | 62797 | 0
LTC06962 | 2000-11-15 | 12 | 0 | 5 | 0 | 0 | 124 | 702 | 8267 | 65059 | 5
LTC06962 | 2001-11-14 | 15 | 2 | 4 | 1 | 0 | 35 | 476 | 20637 | 59399 | 7
LTC06962 | 2002-11-04 | 19 | 0 | 0 | 1 | 7 | 0 | 491 | 28279 | 73152 | 1
LTC06962 | 2003-10-13 | 18 | 0 | 0 | 1 | 0 | 32 | 471 | 25338 | 63558 | 1
LTC06962 | 2004-10-25 | 5 | 0 | 0 | 0 | 0 | 13 | 372 | 28414 | 74024 | 0
LTC06963 | 1993-09-22 | 77 | 0 | 0 | 28 | 238 | 22 | 464 | 33759 | 73632 | 28
LTC06963 | 1997-06-24 | 65 | 5 | 0 | 18 | 144 | 134 | 595 | 26659 | 74595 | 23
LTC06963 | 1998-10-22 | 110 | 17 | 0 | 14 | 171 | 48 | 400 | 22520 | 58508 | 31
LTC06963 | 1999-08-04 | 133 | 28 | 0 | 50 | 447 | 0 | 393 | 26412 | 63104 | 78
LTC06963 | 2000-10-10 | 136 | 23 | 4 | 58 | 5.2 | 28 | 439 | 28842 | 66062 | 85
LTC06963 | 2002-11-01 | 135 | 25 | 5 | 72 | 604 | 64 | 509 | 30420 | 71367 | 102
LTC06963 | 2003-09-05 | 133 | 18 | 2 | 64 | 506 | 17 | 391 | 29614 | 68737 | 84
LTC06963 | 2004-08-17 | 19 | 4 | 1 | 26 | 100 | 26 | 463 | 35149 | 81865 | 31
LTC07145 | 1993-09-14 | 59 | 0 | 0 | 10 | 102 | 74 | 617 | 22553 | 68279 | 10
LTC07145 | 1994-06-01 | 39 | 0 | 5 | 10 | 69 | 50 | 395 | 29477 | 68912 | 15
LTC07145 | 1997-07-18 | 117 | 10 | 2 | 18 | 168 | 264 | 934 | 11139 | 68990 | 30
LTC07145 | 1998-09-02 | 30 | 5 | 0 | 21 | 60 | 13 | 349 | 28200 | 68133 | 26
LTC07145 | 1999-09-03 | 29 | 3 | 0 | 5 | 55 | 29 | 498 | 25987 | 67796 | 8
LTC07145 | 2000-08-23 | 18 | 2 | 0 | 6 | 45 | 14 | 344 | 23278 | 65187 | 8
LTC07145 | 2002-10-16 | 19 | 0 | 0 | 6 | 38 | 0 | 329 | 27275 | 66162 | 6
LTC07145 | 2003-12-18 | 18 | 0 | 0 | 1 | 47 | 11 | 378 | 31164 | 70312 | 1
LTC07145 | 2004-08-27 | 16 | 2 | 0 | 6 | 44 | 19 | 321 | 31310 | 76711 | 8
LTC07146 | 1993-09-08 | 10 | 0 | 0 | 6 | 36 | 80 | 406 | 27816 | 68014 | 6
LTC07146 | 1994-06-10 | 23 | 0 | 0 | 7 | 55 | 141 | 465 | 29020 | 72506 | 7
LTC07146 | 1998-06-17 | 42 | 6 | 0 | 13 | 69 | 36 | 424 | 26882 | 69785 | 19
LTC07146 | 1999-07-20 | 26 | 2 | 0 | 4 | 24 | 38 | 396 | 25232 | 68086 | 6
LTC07146 | 2000-07-03 | 4 | 0 | 0 | 0 | 0 | 38 | 387 | 26821 | 71981 | 0
LTC07146 | 2002-09-04 | 18 | 0 | 0 | 1 | 4 | 94 | 472 | 26707 | 67088 | 1
LTC07146 | 2003-09-02 | 10 | 0 | 1 | 0 | 6 | 32 | 387 | 28100 | 72528 | 1
LTC07146 | 2004-08-18 | 8 | 1 | 0 | 0 | 0 | 63 | 447 | 27317 | 76820 | 1
LTC08077 | 1993-09-07 | 45 | 0 | 0 | 18 | 157 | 42 | 337 | 27768 | 58216 | 18
LTC08077 | 1993-10-12 | 32 | 0 | 3 | 22 | 145 | 49 | 526 | 31353 | 69326 | 25
LTC08077 | 1994-06-14 | 28 | 0 | 0 | 15 | 97 | 38 | 418 | 34991 | 80183 | 15
LTC08077 | 1997-07-01 | 35 | 4 | 3 | 19 | 115 | 87 | 499 | 26895 | 70920 | 26
LTC08077 | 1998-09-01 | 41 | 6 | 0 | 16 | 131 | 152 | 536 | 20697 | 68623 | 22
LTC08077 | 1999-09-09 | 48 | 9 | 0 | 20 | 150 | 14 | 368 | 27733 | 64408 | 29
LTC08077 | 2000-08-29 | 46 | 7 | 0 | 18 | 161 | 0 | 358 | 28576 | 66137 | 25
LTC08077 | 2001-10-19 | 18 | 11 | 0 | 23 | 107 | 29 | 380 | 13290 | 41369 | 34
LTC08077 | 2002-10-23 | 26 | 5 | 0 | 19 | 121 | 0 | 328 | 32352 | 71115 | 24
LTC08077 | 2003-09-18 | 40 | 6 | 0 | 21 | 171 | 25 | 422 | 25840 | 65399 | 27
LTC08077 | 2004-09-15 | 22 | 4 | 0 | 14 | 87 | 12 | 341 | 30251 | 70186 | 18
LTC08077 | 2006-03-08 | 3 | 5 | 0 | 12 | 6 | 24 | 454 | 19505 | 52886 | 17
LTC09580 | 1993-08-16 | 23 | 0 | 0 | 23 | 73 | 48 | 613 | 30624 | 84808 | 23
LTC09580 | 2000-02-01 | 23 | 6 | 0 | 20 | 128 | 6 | 408 | 28585 | 64151 | 26
LTC09580 | 2001-03-13 | 20 | 3 | 0 | 14 | 101 | 38 | 383 | 28002 | 67699 | 17
LTC09580 | 2001-10-30 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 22963 | 70144 | 0
LTC09580 | 2002-02-22 | 8 | 0 | 0 | 0 | 16 | 39 | 353 | 24882 | 59377 | 0
LTC09580 | 2004-02-13 | 24 | 0 | 0 | 8 | 79 | 8 | 392 | 29086 | 64400 | 8
LTC09580 | 2005-02-04 | 5 | 0 | 2 | 1 | 13 | 6 | 383 | 28069 | 63241 | 3
LTC09580 | 2006-03-20 | 4 | 3 | 0 | 2 | 0 | 20 | 501 | 22411 | 59406 | 5
LTC09844 | 1993-09-22 | 208 | 0 | 6 | 38 | 410 | 0 | 508 | 23735 | 67533 | 44
LTC09844 | 1996-03-13 | 25 | 5 | 0 | 10 | 110 | 36 | 466 | 29372 | 63843 | 15
LTC09844 | 1997-05-08 | 47 | 4 | 0 | 13 | 143 | 8 | 470 | 30672 | 69856 | 17
LTC09844 | 1998-06-23 | 13 | 0 | 1 | 3 | 16 | 28 | 442 | 26959 | 73704 | 4
LTC09844 | 2000-07-25 | 5 | 0 | 0 | 0 | 11 | 0 | 328 | 27894 | 70304 | 0
LTC09844 | 2001-10-11 | 26 | 12 | 0 | 25 | 142 | 259 | 663 | 9535 | 47805 | 37
LTC09844 | 2002-11-25 | 181 | 2 | 2 | 4 | 17 | 225 | 891 | 7824 | 77531 | 8
LTC09844 | 2003-09-15 | 216 | 0 | 0 | 2 | 14 | 181 | 1001 | 17888 | 76923 | 2
LTC09844 | 2004-10-06 | 90 | 0 | 0 | 2 | 9 | 138 | 842 | 22022 | 72070 | 2
LTC09846 | 1993-09-07 | 232 | 531 | 3 | 48 | 384 | 122 |  | 29422 | 95007 | 582
LTC09846 | 1993-10-12 | 374 | 17 | 5 | 93 | 759 | 161 | 875 | 10215 | 67692 | 115
LTC09846 | 1994-06-14 | 74 | 0 | 0 | 4 | 60 | 101 | 622 | 30599 | 77426 | 4
LTC09846 | 1996-04-08 | 88 | 20 | 5 | 30 | 152 | 35 | 518 | 29846 | 65891 | 55
LTC09846 | 1997-05-23 | 36 | 3 | 0 | 12 | 76 | 73 | 617 | 23150 | 60163 | 15
LTC09846 | 1998-05-01 | 16 | 2 | 6 | 5 | 31 | 28 | 413 | 28671 | 67595 | 13
LTC09846 | 1999-05-24 | 9 | 0 | 0 | 0 | 0 | 47 | 500 | 25154 | 70910 | 0
LTC09846 | 2000-05-05 | 7 | 0 | 0 | 2 | 0 | 27 | 439 | 28876 | 70430 | 2
LTC09846 | 2002-06-18 | 0 | 0 | 0 | 0 | 0 | 0 | 324 | 30334 | 70492 | 0
LTC09846 | 2003-05-28 | 14 | 4 | 0 | 5 | 24 | 12 | 334 | 29084 | 68495 | 9
LTC09846 | 2005-06-17 | 35 | 0 | 3 | 15 | 104 | 19 | 352 | 37137 | 68456 | 18
LTC10044 | 1993-09-30 | 76 | 0 | 2 | 13 | 82 | 77 | 480 | 30595 | 71366 | 15
LTC10044 | 1994-06-15 | 61 | 0 | 5 | 10 | 54 | 102 | 647 | 26677 | 69958 | 15
LTC10044 | 1997-05-14 | 46 | 0 | 4 | 5 | 41 | 63 | 663 | 23706 | 70305 | 9
LTC10044 | 1999-06-08 | 29 | 0 | 0 | 5 | 8 | 165 | 684 | 16593 | 72371 | 5
LTC10044 | 2000-04-27 | 23 | 0 | 0 | 3 | 22 | 57 | 595 | 23517 | 68177 | 3
LTC10044 | 2002-06-25 | 63 | 0 | 0 | 8 | 34 | 40 | 526 | 25638 | 69727 | 8
LTC10044 | 2003-06-09 | 47 | 0 | 2 | 7 | 26 | 91 | 592 | 22735 | 70132 | 9
LTC10044 | 2004-05-18 | 20 | 0 | 0 | 4 | 6 | 66 | 484 | 26589 | 67851 | 4
LTC10044 | 2005-05-26 | 36 | 0 | 4 | 10 | 33 | 99 | 481 | 26144 | 69611 | 14
LTC10044 | 2006-05-15 | 28 | 8 | 3 | 14 | 38 | 80 | 663 | 18998 | 62399 | 25
LTC10098 | 1993-08-17 | 50 | 0 | 0 | 0 | 0 | 125 | 79 | 27110 | 71405 | 0
LTC10098 | 1994-06-23 | 44 | 0 | 0 | 9 | 51 | 110 | 627 | 26332 | 65851 | 9
LTC10098 | 1995-08-14 | 172 | 20 | 7 | 22 | 178 | 238 | 955 | 26215 | 72939 | 49
LTC10098 | 1996-03-05 | 16 | 1 | 2 | 6 | 38 | 72 | 640 | 27058 | 68950 | 9
LTC10098 | 1997-05-21 | 50 | 6 | 3 | 16 | 102 | 132 | 766 | 25966 | 70005 | 25
LTC10098 | 1998-03-16 | 20 | 0 | 0 | 6 | 43 | 19 | 418 | 28799 | 69318 | 6
LTC10098 | 1999-04-13 | 10 | 3 | 0 | 5 | 22 | 0 | 309 | 29570 | 68208 | 8
LTC10098 | 2000-03-30 | 5 | 0 | 0 | 0 | 7 | 13 | 345 | 29354 | 66291 | 0
LTC10098 | 2001-05-24 | 9 | 2 | 0 | 3 | 14 | 9 | 357 | 27348 | 67287 | 5
LTC10098 | 2002-05-15 | 6 | 0 | 0 | 6 | 19 | 8 | 336 | 32137 | 74463 | 6
LTC10098 | 2003-05-29 | 12 | 0 | 0 | 4 | 29 | 0 | 336 | 28922 | 66109 | 4
LTC10098 | 2004-05-05 | 11 | 0 | 0 | 5 | 20 | 8 | 312 | 29193 | 70482 | 5
LTC10098 | 2005-05-19 | 18 | 0 | 0 | 8 | 38 | 0 | 314 | 29261 | 69970 | 8
LTC10121 | 2001-03-14 | 66 | 28 | 15 | 174 | 554 | 55 | 819 | 26982 | 65750 | 217
LTC10121 | 2001-11-19 | 0 | 14 | 0 | 1 | 0 | 16 | 295 | 20964 | 51995 | 15
LTC10121 | 2002-03-07 | 88 | 36 | 4 | 83 | 368 | 12 | 419 | 26269 | 61776 | 123
LTC10121 | 2003-04-10 | 103 | 61 | 15 | 245 | 923 | 46 | 779 | 26582 | 60880 | 321
LTC10121 | 2004-03-23 | 144 | 74 | 20 | 294 | 1082 | 57 | 944 | 27924 | 71925 | 388
LTC10121 | 2005-03-21 | 403 | 192 | 57 | 815 | 2602 | 61 | 1106 | 29603 | 70010 | 1064
LTC10121 | 2006-03-20 | 65 | 34 | 5 | 71 | 390 | 27 | 491 | 21535 | 60911 | 110
LTC10131 | 1993-08-17 | 73 | 0 | 0 | 14 | 73 | 172 | 858 | 22530 | 71258 | 14
LTC10131 | 1994-06-10 | 49 | 0 | 0 | 7 | 53 | 237 | 709 | 24989 | 70274 | 7
LTC10131 | 1995-08-04 | 90 | 14 | 0 | 19 | 152 | 158 | 806 | 29059 | 81089 | 33
LTC10131 | 1996-03-13 | 98 | 4 | 0 | 11 | 60 | 60 | 537 | 34028 | 76285 | 15
LTC10131 | 1997-05-22 | 55 | 4 | 2 | 16 | 101 | 49 | 507 | 30611 | 69385 | 22
LTC10131 | 1998-02-13 | 63 | 13 | 16 | 28 | 144 | 33 | 418 | 28914 | 71235 | 57
LTC10131 | 1999-03-25 | 22 | 2 | 1 | 3 | 15 | 32 | 431 | 27830 | 67405 | 6
LTC10131 | 2000-03-08 | 32 | 0 | 0 | 4 | 16 | 42 | 522 | 27270 | 70222 | 4
LTC10131 | 2001-03-14 | 27 | 2 | 0 | 3 | 43 | 46 | 483 | 25293 | 67636 | 5
LTC10131 | 2002-03-06 | 51 | 0 | 0 | 3 | 27 | 42 | 624 | 24389 | 65076 | 3
LTC10131 | 2003-04-09 | 28 | 1 | 0 | 4 | 2 | 58 | 367 | 23644 | 58583 | 5
LTC10131 | 2004-03-18 | 43 | 0 | 1 | 3 | 21 | 101 | 637 | 21111 | 67906 | 4
LTC10131 | 2005-03-18 | 32 | 0 | 0 | 5 | 28 | 64 | 507 | 25108 | 67589 | 5
LTC10131 | 2006-03-20 | 68 | 7 | 0 | 8 | 37 | 61 | 671 | 22872 | 65653 | 15
LTC10145 | 1993-08-17 | 27 | 0 | 12 | 55 | 34 | 69 | 476 | 28547 | 69261 | 67
LTC10145 | 1994-05-25 | 24 | 0 | 0 | 9 | 38 | 46 | 370 | 30749 | 68030 | 9
LTC10145 | 1994-06-23 | 25 | 0 | 0 | 10 | 43 | 65 | 363 | 34164 | 79713 | 10
LTC10145 | 1994-07-26 | 12 | 0 | 6 | 10 | 43 | 56 | 420 | 32383 | 74087 | 16
LTC10145 | 1994-08-24 | 14 | 0 | 0 | 13 | 37 | 80 | 500 | 26499 | 66943 | 13
LTC10145 | 1995-08-09 | 16 | 3 | 0 | 7 | 56 | 120 | 544 | 26474 | 68786 | 10
LTC10145 | 1996-03-04 | 4 | 2 | 0 | 6 | 31 | 49 | 549 | 30080 | 69283 | 8
LTC10145 | 1997-05-21 | 28 | 4 | 1 | 16 | 81 | 49 | 486 | 29110 | 70383 | 21
LTC10145 | 1998-07-30 | 40 | 7 | 1 | 13 | 60 | 74 | 571 | 27305 | 76031 | 21
LTC10145 | 1999-08-05 | 7 | 0 | 0 | 2 | 11 | 0 | 283 | 25748 | 68317 | 2
LTC10145 | 2000-07-27 | 5 | 0 | 0 | 0 | 5 | 0 | 269 | 27286 | 64518 | 0
LTC10145 | 2002-10-04 | 11 | 0 | 0 | 3 | 12 | 0 | 296 | 26669 | 61358 | 3
LTC10145 | 2003-09-02 | 11 | 0 | 1 | 0 | 18 | 20 | 296 | 29533 | 70139 | 1
LTC10145 | 2004-08-30 | 12 | 3 | 0 | 3 | 17 | 11 | 305 | 31462 | 75578 | 6
LTC10158 | 1990-06-15 | 65 | 0 | 0 | 7 | 38 | 156 | 732 | 21864 | 72854 | 7
LTC10158 | 1990-09-07 | 60 | 0 | 0 | 8 | 39 | 38 | 539 | 28828 | 66744 | 8
LTC10158 | 1996-03-12 | 19 | 0 | 0 | 4 | 29 | 26 | 658 | 60462 | 177308 | 4
LTC10158 | 1997-05-22 | 42 | 3 | 2 | 11 | 76 | 35 | 502 | 26381 | 68141 | 16
LTC10158 | 1997-08-08 | 92 | 8 | 0 | 19 | 158 | 158 | 656 | 26918 | 69107 | 27
LTC10158 | 1998-01-30 | 47 | 6 | 0 | 12 | 98 | 32 | 438 | 27028 | 67237 | 18
LTC10158 | 1998-03-10 | 58 | 6 | 0 | 18 | 117 | 70 | 590 | 21185 | 68171 | 24
LTC10158 | 1999-02-17 | 27 | 4 | 0 | 5 | 44 | 43 | 465 | 21715 | 63510 | 9
LTC10158 | 1999-05-19 | 25 | 3 | 0 | 35 | 35 | 45 | 492 | 25238 | 71116 | 38
LTC10158 | 2000-03-28 | 23 | 0 | 1 | 0 | 9 | 36 | 436 | 27856 | 71665 | 1
LTC10158 | 2001-04-23 | 33 | 0 | 0 | 4 | 26 | 10 | 631 | 25207 | 69285 | 4
LTC10158 | 2002-08-01 | 75 | 0 | 4 | 4 | 28 | 217 | 1037 | 13371 | 67076 | 8
LTC10158 | 2003-05-28 | 54 | 0 | 0 | 2 | 30 | 131 | 740 | 20544 | 71690 | 2
LTC10158 | 2004-05-05 | 42 | 0 | 0 | 1 | 1 | 85 | 562 | 22671 | 65012 | 1
LTC10158 | 2005-06-06 | 10 | 0 | 0 | 3 | 16 | 8 | 324 | 28852 | 72374 | 3
LTC10158 | 2006-05-17 | 21 | 2 | 0 | 2 | 15 | 10 | 353 | 20894 | 55257 | 4
LTC10171 | 1993-08-17 | 276 | 1833 | 505 | 3731 | 149 | 428 | 1211 | 17155 | 74832 | 6069
LTC10171 | 1993-08-26 | 280 | 2026 | 588 | 4434 | 163 | 439 | 979 | 24893 | 81857 | 7048
LTC10171 | 1993-09-03 | 375 | 3802 | 1422 | 8343 | 211 | 476 | 1084 | 23162 | 77896 | 13567
LTC10171 | 1993-09-13 | 445 | 4449 | 1736 | 10526 | 274 | 1113 | 822 | 28761 | 77418 | 16711
LTC10171 | 1993-09-21 | 469 | 5440 | 2173 | 13424 | 360 | 372 | 783 | 26493 | 82095 | 21037
LTC10171 | 1994-05-26 | 18 | 0 | 0 | 6 | 36 | 0 | 443 | 32792 | 69117 | 6
LTC10171 | 1994-06-23 | 27 | 0 | 0 | 9 | 56 | 21 | 341 | 31627 | 68516 | 9
LTC10171 | 1994-07-26 | 11 | 0 | 0 | 10 | 48 | 19 | 346 | 32079 | 70200 | 10
LTC10171 | 1994-08-24 | 13 | 0 | 7 | 9 | 30 | 46 | 351 | 32980 | 70051 | 16
LTC10171 | 1995-08-14 | 25 | 5 | 0 | 16 | 80 | 19 | 367 | 32499 | 72038 | 21
LTC10171 | 1996-02-26 | 9 | 2 | 1 | 10 | 58 | 29 | 481 | 31482 | 67872 | 13
LTC10171 | 1997-05-21 | 20 | 3 | 0 | 14 | 62 | 47 | 558 | 29932 | 72162 | 17
LTC10171 | 1998-07-30 | 35 | 4 | 0 | 17 | 43 | 125 | 585 | 17905 | 73988 | 21
LTC10171 | 1999-08-09 | 18 | 3 | 0 | 8 | 35 | 71 | 398 | 26836 | 77637 | 11
LTC10171 | 2000-07-27 | 3 | 0 | 0 | 0 | 0 | 0 | 426 | 28107 | 66279 | 0
LTC10171 | 2002-10-03 | 8 | 0 | 0 | 3 | 9 | 0 | 329 | 26338 | 66807 | 3
LTC10171 | 2003-09-03 | 22 | 0 | 2 | 17 | 51 | 0 | 291 | 28558 | 65259 | 19
LTC10171 | 2004-08-30 | 12 | 2 | 0 | 4 | 12 | 11 | 296 | 30642 | 74794 | 6
LTC10184 | 1993-08-17 | 126 | 0 | 10 | 20 | 119 | 179 | 964 | 17630 | 65302 | 30
LTC10184 | 1994-06-10 | 91 | 0 | 9 | 15 | 102 | 219 | 718 | 23779 | 69088 | 24
LTC10184 | 1995-08-04 | 0 | 10 | 12 | 11 | 50 | 27 | 444 | 34376 | 82087 | 33
LTC10184 | 1996-03-13 | 139 | 12 | 2 | 22 | 164 | 17 | 440 | 30095 | 68993 | 36
LTC10184 | 1997-06-05 | 38 | 4 | 0 | 11 | 82 | 0 | 428 | 28405 | 67400 | 15
LTC10184 | 1998-11-02 | 53 | 5 | 0 | 7 | 50 | 13 | 397 | 25919 | 68654 | 12
LTC10184 | 1999-10-20 | 78 | 5 | 0 | 10 | 65 | 18 | 417 | 24105 | 62804 | 15
LTC10184 | 2000-12-04 | 234 | 3 | 0 | 8 | 50 | 80 | 623 | 21229 | 71948 | 11
LTC10184 | 2001-05-24 | 357 | 5 | 0 | 6 | 68 | 182 | 780 | 15601 | 77225 | 11
LTC10184 | 2001-10-25 | 140 | 13 | 0 | 22 | 104 | 102 | 746 | 8856 | 37845 | 35
LTC10184 | 2002-12-04 | 138 | 4 | 0 | 10 | 66 | 0 | 440 | 27360 | 72887 | 14
LTC10184 | 2003-11-03 | 41 | 3 | 0 | 4 | 22 | 57 | 487 | 30209 | 78078 | 7
LTC10184 | 2004-10-26 | 50 | 2 | 0 | 3 | 20 | 41 | 465 | 30868 | 75896 | 5
LTC10185 | 1993-08-13 | 56 | 0 | 0 | 9 | 63 | 107 | 625 | 30216 | 76411 | 9
LTC10185 | 1994-06-07 | 34 | 0 | 0 | 8 | 36 | 84 | 454 | 27559 | 67693 | 8
LTC10185 | 1995-08-16 | 72 | 5 | 0 | 13 | 67 | 156 | 745 | 27077 | 70199 | 18
LTC10185 | 1996-03-20 | 27 | 0 | 0 | 11 | 37 | 27 | 573 | 34077 | 73711 | 11
LTC10185 | 1997-05-27 | 18 | 0 | 0 | 5 | 30 | 40 | 540 | 29098 | 68483 | 5
LTC10185 | 1998-07-23 | 95 | 4 | 0 | 12 | 42 | 176 | 1370 | 12597 | 69420 | 16
LTC10185 | 1999-06-18 | 42 | 47 | 3 | 27 | 37 | 119 | 567 | 29984 | 84401 | 77
LTC10185 | 1999-08-03 | 286 | 1366 | 508 | 3969 | 263 | 508 | 988 | 19001 | 67017 | 5843
LTC10185 | 1999-08-13 | 7 | 0 | 0 | 2 | 9 | 0 | 350 | 25057 | 61470 | 2
LTC10185 | 1999-08-20 | 12 | 0 | 0 | 2 | 17 | 0 | 291 | 26978 | 64763 | 2
LTC10185 | 1999-10-26 | 4 | 0 | 0 | 0 | 0 | 0 | 367 | 22583 | 60605 | 0
LTC10185 | 2000-06-13 | 3 | 0 | 4 | 1 | 0 | 0 | 285 | 28652 | 68954 | 5
LTC10185 | 2002-07-11 | 3 | 0 | 0 | 1 | 9 | 6 | 219 | 25004 | 69277 | 1
LTC10185 | 2003-07-18 | 6 | 0 | 0 | 2 | 10 | 0 | 296 | 25454 | 62798 | 2
LTC10185 | 2004-06-24 | 6 | 0 | 0 | 1 | 6 | 0 | 277 | 26074 | 61441 | 1
LTC10185 | 2005-06-23 | 5 | 0 | 0 | 3 | 4 | 14 | 301 | 28528 | 67998 | 3
LTC10195 | 1993-08-17 | 52 | 0 | 0 | 8 | 56 | 92 | 572 | 28886 | 68687 | 8
LTC10195 | 1994-05-26 | 62 | 0 | 0 | 7 | 53 | 170 | 499 | 26813 | 67274 | 7
LTC10195 | 1994-06-23 | 60 | 0 | 0 | 8 | 57 | 128 | 648 | 26378 | 69619 | 8
LTC10195 | 1994-07-26 | 60 | 0 | 0 | 23 | 73 | 108 | 609 | 29594 | 72395 | 23
LTC10195 | 1994-08-24 | 54 | 0 | 0 | 8 | 64 | 98 | 703 | 30256 | 72939 | 8
LTC10195 | 1995-08-14 | 75 | 4 | 0 | 14 | 68 | 168 | 759 | 25236 | 70999 | 18
LTC10195 | 1996-03-05 | 15 | 2 | 0 | 5 | 40 | 46 | 601 | 29945 | 70766 | 7
LTC10195 | 1997-05-21 | 42 | 5 | 3 | 18 | 44 | 35 | 618 | 31690 | 72189 | 26
LTC10195 | 1998-04-16 | 39 | 3 | 2 | 7 | 46 | 25 | 437 | 26277 | 72794 | 12
LTC10195 | 1999-06-16 | 71 | 10 | 4 | 18 | 99 | 99 | 574 | 22826 | 64080 | 32
LTC10195 | 2000-05-16 | 112 | 13 | 0 | 26 | 146 | 79 | 491 | 24981 | 65235 | 39
LTC10195 | 2001-06-14 | 53 | 2 | 0 | 11 | 35 | 104 | 636 | 23924 | 71246 | 13
LTC10195 | 2002-06-12 | 54 | 6 | 1 | 19 | 90 | 0 | 762 | 20913 | 68683 | 26
LTC10195 | 2003-06-04 | 54 | 6 | 0 | 9 | 46 | 93 | 637 | 21568 | 70189 | 15
LTC10195 | 2004-06-02 | 85 | 4 | 0 | 10 | 42 | 103 | 642 | 24814 | 67098 | 14
LTC10195 | 2004-09-23 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 16325 | 83040 | 0
LTC10195 | 2005-05-25 | 18 | 0 | 2 | 6 | 34 | 19 | 405 | 26500 | 69319 | 8
LTC10216 | 1993-08-16 | 21 | 0 | 3 | 6 | 22 | 59 | 571 | 24901 | 76718 | 9
LTC10216 | 1994-06-07 | 11 | 0 | 0 | 5 | 39 | 53 | 408 | 23174 | 66828 | 5
LTC10216 | 1995-08-16 | 28 | 4 | 0 | 9 | 49 | 82 | 671 | 28577 | 69930 | 13
LTC10216 | 1996-04-10 | 4 | 0 | 0 | 0 | 28 | 44 | 544 | 26838 | 74976 | 0
LTC10216 | 1997-05-23 | 12 | 4 | 0 | 5 | 61 | 125 | 800 | 15642 | 72985 | 9
LTC10216 | 1998-01-29 | 9 | 0 | 0 | 3 | 21 | 22 | 367 | 25502 | 66793 | 3
LTC10216 | 1999-03-02 | 3 | 0 | 1 | 2 | 2 | 23 | 431 | 27243 | 66605 | 3
LTC10216 | 2000-02-28 | 6 | 0 | 0 | 2 | 6 | 11 | 394 | 28733 | 68006 | 2
LTC10216 | 2001-04-10 | 4 | 0 | 0 | 2 | 4 | 0 | 320 | 26886 | 59051 | 2
LTC10216 | 2002-01-28 | 3 | 4 | 0 | 0 | 4 | 0 | 313 | 27668 | 60731 | 4
LTC10216 | 2003-03-11 | 13 | 0 | 0 | 10 | 14 | 0 | 423 | 25953 | 58652 | 10
LTC10216 | 2003-03-18 | 8 | 0 | 0 | 8 | 12 | 0 | 414 | 27404 | 61013 | 8
LTC10216 | 2004-02-10 | 7 | 0 | 0 | 3 | 9 | 13 | 366 | 30140 | 64732 | 3
LTC10216 | 2004-03-26 | 2 | 0 | 0 | 2 | 4 | 0 | 327 | 27278 | 60135 | 2
LTC10216 | 2004-06-15 | 4 | 3 | 0 | 0 | 0 | 1 | 319 | 26862 | 66975 | 3
LTC10216 | 2005-02-28 | 8 | 0 | 0 | 3 | 3 | 12 | 356 | 29923 | 65768 | 3
LTC10267 | 1993-09-07 | 54 | 0 | 0 | 1 | 22 | 118 | 661 | 27770 | 73682 | 1
LTC10267 | 1994-06-16 | 105 | 0 | 7 | 19 | 120 | 153 | 869 | 22099 | 74019 | 26
LTC10267 | 1996-04-09 | 117 | 8 | 1 | 15 | 118 | 143 | 1024 | 15536 | 62058 | 24
LTC10267 | 1997-05-15 | 70 | 4 | 0 | 8 | 86 | 209 | 1080 | 7169 | 65114 | 12
LTC10267 | 1998-03-26 | 51 | 4 | 0 | 17 | 98 | 34 | 479 | 24000 | 59981 | 21
LTC10267 | 1999-09-30 | 11 | 0 | 0 | 0 | 5 | 0 | 338 | 28269 | 66562 | 0
LTC10267 | 2000-10-10 | 22 | 2 | 0 | 5 | 49 | 0 | 376 | 29155 | 64277 | 7
LTC10267 | 2001-11-12 | 37 | 7 | 0 | 3 | 13 | 45 | 527 | 24442 | 64944 | 10
LTC10267 | 2002-10-23 | 6 | 0 | 0 | 2 | 14 | 0 | 336 | 32621 | 70859 | 2
LTC10267 | 2003-09-30 | 3 | 0 | 0 | 1 | 0 | 19 | 504 | 30042 | 69561 | 1
LTC10267 | 2004-09-29 | 0 | 0 | 3 | 0 | 0 | 8 | 445 | 28875 | 70235 | 3
LTC10289 | 1993-08-16 | 387 | 2794 | 1214 | 7709 | 222 | 134 | 435 | 32951 | 79720 | 11717
LTC10289 | 1993-08-20 | 416 | 2952 | 1235 | 8733 | 301 | 70 | 442 | 27658 | 73425 | 12920
LTC10289 | 1993-08-28 | 513 | 4520 | 2042 | 12346 | 426 | 82 | 534 | 22051 | 75235 | 18908
LTC10289 | 1993-09-21 | 0 | 0 | 9 | 14 | 7 | 0 | 368 | 35591 | 80239 | 23
LTC10289 | 1993-10-26 | 0 | 0 | 0 | 0 | 0 | 28 | 281 | 32175 | 74220 | 0
LTC10289 | 1994-06-03 | 29 | 0 | 7 | 32 | 45 | 39 | 408 | 31354 | 70336 | 39
LTC10289 | 1994-07-07 | 23 | 0 | 0 | 11 | 23 | 23 | 325 | 33262 | 73305 | 11
LTC10289 | 1994-08-03 | 36 | 0 | 0 | 17 | 76 | 0 | 334 | 32894 | 71100 | 17
LTC10289 | 1995-08-21 | 28 | 6 | 0 | 22 | 93 | 77 | 393 | 31053 | 74571 | 28
LTC10289 | 1996-06-27 | 0 | 0 | 1 | 1 | 0 | 0 | 141 | 20213 | 44280 | 2
LTC10289 | 1996-06-27 | 39 | 0 | 0 | 6 | 42 | 0 | 207 | 21593 | 50060 | 6
LTC10289 | 2001-02-19 | 12 | 1 | 0 | 7 | 9 | 21 | 401 | 30302 | 69408 | 8
LTC10289 | 2002-03-04 | 18 | 2 | 0 | 11 | 41 | 50 | 415 | 26795 | 64248 | 13
LTC10289 | 2003-03-25 | 22 | 0 | 0 | 4 | 14 | 72 | 525 | 18715 | 68811 | 4
LTC10289 | 2004-02-23 | 21 | 0 | 0 | 5 | 31 | 34 | 386 | 24740 | 61319 | 5
LTC10289 | 2005-04-10 | 4 | 0 | 3 | 4 | 0 | 52 | 266 | 10485 | 51555 | 7
LTC10289 | 2005-05-24 | 20 | 0 | 0 | 6 | 28 | 0 | 305 | 30641 | 71720 | 6
LTC10290 | 1993-08-16 | 623 | 5450 | 1902 | 11833 | 374 | 414 | 1542 | 16399 | 70496 | 19185
LTC10290 | 1993-08-26 | 510 | 4474 | 1575 | 8504 | 243 | 514 | 1833 | 15579 | 73725 | 14553
LTC10290 | 1993-09-21 | 33 | 0 | 1 | 9 | 73 | 0 | 321 | 32759 | 75374 | 10
LTC10290 | 1993-11-08 | 17 | 0 | 12 | 10 | 43 | 0 | 360 | 35793 | 77509 | 22
LTC10290 | 1994-06-03 | 27 | 0 | 2 | 10 | 54 | 22 | 294 | 31718 | 69843 | 12
LTC10290 | 1994-07-07 | 17 | 0 | 0 | 13 | 61 | 0 | 299 | 34655 | 72680 | 13
LTC10290 | 1995-08-16 | 31 | 9 | 0 | 14 | 108 | 89 | 514 | 27692 | 75718 | 23
LTC10290 | 1996-04-11 | 15 | 0 | 0 | 10 | 40 | 52 | 450 | 29634 | 71245 | 10
LTC10290 | 1997-05-20 | 29 | 4 | 0 | 14 | 68 | 45 | 436 | 30356 | 71606 | 18
LTC10290 | 1998-06-11 | 23 | 0 | 2 | 9 | 55 | 39 | 400 | 25291 | 67130 | 11
LTC10290 | 2000-07-03 | 30 | 3 | 0 | 7 | 47 | 76 | 497 | 24859 | 74961 | 10
LTC10290 | 2001-06-18 | 14 | 3 | 0 | 8 | 23 | 28 | 344 | 27212 | 71459 | 11
LTC10290 | 2002-06-24 | 30 | 0 | 0 | 6 | 33 | 95 | 414 | 26746 | 70743 | 6
LTC10290 | 2003-08-07 | 31 | 0 | 0 | 9 | 45 | 69 | 415 | 26318 | 72193 | 9
LTC10290 | 2004-07-21 | 35 | 4 | 0 | 6 | 36 | 248 | 680 | 7376 | 72416 | 10
LTC10290 | 2005-03-23 | 10 | 6 | 0 | 6 | 0 | 34 | 1866 | 15879 | 71220 | 12
LTC10290 | 2005-04-03 | 286 | 56 | 10 | 137 | 388 | 63 | 930 | 20537 | 63032 | 203
LTC10290 | 2006-04-06 | 2 | 3 | 0 | 5 | 5 | 8 | 451 | 23603 | 61541 | 8
LTC10290 | 2006-05-26 | 12 | 2 | 0 | 3 | 14 | 14 | 417 | 25020 | 69457 | 5
LTC10294 | 1993-08-13 | 112 | 0 | 0 | 17 | 46 | 442 | 908 | 23075 | 69354 | 17
LTC10294 | 1994-05-26 | 77 | 0 | 0 | 8 | 35 | 119 | 611 | 23293 | 63134 | 8
LTC10294 | 1994-06-23 | 78 | 0 | 0 | 11 | 39 | 204 | 778 | 21340 | 66672 | 11
LTC10294 | 1994-07-26 | 70 | 0 | 2 | 8 | 48 | 220 | 916 | 20812 | 66394 | 10
LTC10294 | 1994-08-04 | 64 | 0 | 0 | 9 | 40 | 124 | 757 | 24534 | 69750 | 9
LTC10294 | 1995-08-16 | 23 | 3 | 0 | 14 | 55 | 21 | 403 | 30592 | 70030 | 17
LTC10294 | 1996-03-20 | 30 | 0 | 0 | 17 | 79 | 6 | 557 | 31096 | 64588 | 17
LTC10294 | 1997-05-27 | 13 | 0 | 0 | 12 | 43 | 0 | 416 | 30473 | 70639 | 12
LTC10294 | 1998-12-31 | 5 | 1 | 0 | 4 | 11 | 0 | 256 | 27421 | 66040 | 5
LTC10294 | 1999-11-16 | 12 | 0 | 0 | 4 | 15 | 0 | 310 | 28962 | 66896 | 4
LTC10294 | 2001-01-24 | 11 | 1 | 0 | 6 | 25 | 8 | 339 | 27654 | 62347 | 7
LTC10294 | 2001-12-05 | 4 | 3 | 7 | 4 | 0 | 7 | 415 | 24590 | 53933 | 14
LTC10294 | 2002-12-05 | 8 | 0 | 0 | 4 | 24 | 0 | 344 | 31851 | 70893 | 4
LTC10294 | 2003-12-17 | 9 | 4 | 0 | 6 | 25 | 31 | 407 | 22129 | 60850 | 10
LTC10294 | 2004-12-22 | 10 | 4 | 0 | 7 | 24 | 3 | 370 | 29054 | 63300 | 11
LTC10294 | 2006-05-23 | 458 | 166 | 21 | 308 | 1315 | 25 | 392 | 19992 | 56564 | 495
LTC10294 | 2006-05-30 | 22 | 5 | 1 | 14 | 27 | 29 | 458 | 19014 | 62922 | 20
LTC10300 | 1993-08-17 | 35 | 0 | 0 | 14 | 77 | 49 | 353 | 34471 | 78394 | 14
LTC10300 | 1994-05-25 | 68 | 0 | 0 | 14 | 97 | 55 | 354 | 29671 | 72955 | 14
LTC10300 | 1994-06-23 | 76 | 0 | 0 | 19 | 154 | 42 | 360 | 34244 | 78999 | 19
LTC10300 | 1994-07-26 | 61 | 0 | 0 | 19 | 186 | 15 | 388 | 33191 | 74892 | 19
LTC10300 | 1994-08-24 | 43 | 0 | 0 | 17 | 124 | 45 | 356 | 31724 | 73005 | 17
LTC10300 | 1995-08-10 | 19 | 3 | 0 | 16 | 68 | 63 | 450 | 30519 | 71766 | 19
LTC10300 | 1996-02-29 | 3 | 1 | 0 | 7 | 37 | 53 | 497 | 29249 | 68479 | 8
LTC10300 | 1997-05-21 | 28 | 0 | 0 | 8 | 49 | 69 | 517 | 27802 | 71181 | 8
LTC10300 | 1999-09-08 | 65 | 9 | 0 | 14 | 82 | 129 | 499 | 21107 | 70496 | 23
LTC10300 | 2000-09-12 | 33 | 6 | 0 | 10 | 59 | 8 | 416 | 25832 | 64570 | 16
LTC10300 | 2002-10-10 | 26 | 4 | 0 | 9 | 39 | 0 | 347 | 27314 | 66904 | 13
LTC10300 | 2003-09-24 | 26 | 5 | 2 | 8 | 37 | 50 | 365 | 27268 | 74314 | 15
LTC10300 | 2004-10-07 | 52 | 5 | 0 | 14 | 55 | 52 | 421 | 27141 | 71956 | 19
LTC10387 | 1993-09-22 | 78 | 0 | 3 | 6 | 33 | 68 | 674 | 28808 | 75388 | 9
LTC10387 | 1994-07-14 | 136 | 0 | 8 | 31 | 31 | 191 | 1085 | 17140 | 69817 | 39
LTC10387 | 1996-03-14 | 297 | 0 | 3 | 5 | 34 | 88 | 755 | 29810 | 75953 | 8
LTC10387 | 1997-05-19 | 72 | 4 | 0 | 5 | 33 | 85 | 871 | 22879 | 68667 | 9
LTC10387 | 1998-11-12 | 9 | 16 | 5 | 6 | 0 | 20 | 237 | 19428 | 68825 | 27
LTC10387 | 1999-10-06 | 5 | 0 | 0 | 2 | 15 | 0 | 394 | 28991 | 68400 | 2
LTC10387 | 2000-10-10 | 12 | 8 | 0 | 18 | 155 | 20 | 404 | 27645 | 68078 | 26
LTC10387 | 2001-11-28 | 0 | 0 | 0 | 1 | 1 | 15 | 348 | 23665 | 50698 | 1
LTC10387 | 2002-11-01 | 7 | 0 | 0 | 0 | 2 | 0 | 352 | 32442 | 73366 | 0
LTC10387 | 2003-10-02 | 3 | 0 | 0 | 0 | 0 | 15 | 458 | 31607 | 74787 | 0
LTC10387 | 2004-10-13 | 2 | 0 | 0 | 0 | 0 | 6 | 351 | 31966 | 72659 | 0
LTC10388 | 1993-09-22 | 88 | 0 | 0 | 6 | 41 | 85 | 705 | 27526 | 70833 | 6
LTC10388 | 1994-07-14 | 154 | 0 | 3 | 3 | 28 | 147 | 987 | 22419 | 72098 | 6
LTC10388 | 1996-03-08 | 43 | 0 | 0 | 0 | 24 | 48 | 569 | 26540 | 65848 | 0
LTC10388 | 1996-03-14 | 323 | 26 | 3 | 20 | 17 | 142 | 1015 | 29068 | 69339 | 49
LTC10388 | 1997-05-19 | 79 | 0 | 0 | 5 | 38 | 110 | 899 | 22083 | 67926 | 5
LTC10388 | 1998-11-12 | 7 | 13 | 7 | 2 | 0 | 27 | 290 | 19091 | 63510 | 22
LTC10388 | 1999-10-07 | 4 | 0 | 0 | 0 | 10 | 0 | 401 | 27157 | 65551 | 0
LTC10388 | 2000-10-10 | 6 | 5 | 0 | 10 | 81 | 0 | 368 | 29976 | 68112 | 15
LTC10388 | 2001-11-28 | 0 | 0 | 0 | 1 | 5 | 9 | 301 | 22102 | 47212 | 1
LTC10388 | 2002-11-01 | 3 | 0 | 0 | 2 | 3 | 0 | 323 | 31913 | 72497 | 2
LTC10388 | 2003-10-02 | 4 | 0 | 3 | 0 | 7 | 18 | 344 | 31537 | 75439 | 3
LTC10388 | 2004-10-13 | 3 | 0 | 0 | 0 | 0 | 6 | 372 | 33706 | 77020 | 0
LTC10430 | 1991-12-13 | 11 | 0 | 0 | 0 | 0 | 27 | 468 | 28507 | 71673 | 0
LTC10430 | 1993-09-27 | 23 | 0 | 6 | 32 | 0 | 85 | 597 | 25120 | 73257 | 38
LTC10430 | 1994-06-06 | 38 | 0 | 3 | 36 | 0 | 0 | 529 | 23545 | 70527 | 39
LTC10430 | 1996-04-23 | 37 | 0 | 1 | 1 | 0 | 52 | 539 | 25933 | 73190 | 2
LTC10430 | 1997-05-20 | 39 | 0 | 0 | 7 | 0 | 15 | 495 | 27487 | 65144 | 7
LTC10430 | 1997-12-30 | 32 | 45 | 10 | 70 | 0 | 33 | 525 | 24391 | 70648 | 125
LTC10430 | 1999-03-18 | 23 | 14 | 5 | 25 | 0 | 48 | 633 | 19760 | 69155 | 44
LTC10430 | 2000-01-31 | 7 | 0 | 0 | 0 | 0 | 12 | 411 | 26590 | 70781 | 0
LTC10430 | 2001-02-20 | 14 | 0 | 0 | 0 | 0 | 23 | 362 | 28056 | 68041 | 0
LTC10430 | 2002-02-20 | 35 | 0 | 0 | 0 | 0 | 48 | 474 | 25657 | 66432 | 0
LTC10430 | 2003-02-20 | 17 | 0 | 1 | 4 | 0 | 0 | 471 | 29145 | 66627 | 5
LTC10430 | 2004-02-03 | 12 | 0 | 0 | 0 | 0 | 20 | 396 | 28358 | 66559 | 0
LTC10430 | 2005-02-07 | 21 | 0 | 0 | 0 | 0 | 46 | 502 | 27343 | 75730 | 0
LTC10452 | 1993-09-23 | 0 | 0 | 0 | 0 | 0 | 377 | 445 | 32003 | 71973 | 0
LTC10452 | 1998-03-04 | 132 | 42 | 3 | 94 | 743 | 42 | 695 | 14716 | 72628 | 139
LTC10452 | 1999-06-08 | 1524 | 162 | 14 | 187 | 1476 | 208 | 676 | 15614 | 53169 | 363
LTC10452 | 2000-03-02 | 2435 | 353 | 18 | 362 | 2716 | 471 | 1070 | 11874 | 52023 | 733
LTC10488 | 1993-08-13 | 187 | 0 | 25 | 104 | 139 | 348 | 1106 | 17286 | 74891 | 129
LTC10488 | 1994-03-04 | 56 | 0 | 6 | 48 | 333 | 65 | 448 | 34721 | 80087 | 54
LTC10488 | 1994-05-26 | 142 | 0 | 0 | 7 | 44 | 214 | 776 | 20812 | 67765 | 7
LTC10488 | 1994-06-23 | 169 | 0 | 0 | 15 | 76 | 390 | 1300 | 14976 | 72938 | 15
LTC10488 | 1994-07-26 | 99 | 0 | 0 | 10 | 67 | 359 | 1149 | 16104 | 66491 | 10
LTC10488 | 1994-08-24 | 88 | 0 | 0 | 8 | 59 | 192 | 883 | 22075 | 67307 | 8
LTC10488 | 1995-08-14 | 198 | 10 | 0 | 21 | 135 | 212 | 929 | 24330 | 73620 | 31
LTC10488 | 1996-03-04 | 30 | 3 | 4 | 7 | 48 | 91 | 671 | 25412 | 64972 | 14
LTC10488 | 1997-05-21 | 11 | 0 | 1 | 12 | 68 | 0 | 450 | 33615 | 72430 | 13
LTC10488 | 1998-11-03 | 13 | 4 | 0 | 14 | 17 | 0 | 347 | 29738 | 70716 | 18
LTC10488 | 1999-10-26 | 15 | 3 | 0 | 15 | 75 | 0 | 347 | 28599 | 65303 | 18
LTC10488 | 2000-11-21 | 9 | 0 | 0 | 12 | 46 | 24 | 363 | 30798 | 74102 | 12
LTC10488 | 2001-10-24 | 21 | 10 | 1 | 33 | 123 | 28 | 436 | 13914 | 42782 | 44
LTC10488 | 2002-03-06 | 9 | 0 | 0 | 11 | 252 | 25 | 324 | 19354 | 50507 | 11
LTC10488 | 2002-12-18 | 22 | 4 | 1 | 24 | 81 | 0 | 392 | 31456 | 72177 | 29
LTC10488 | 2003-09-29 | 14 | 6 | 0 | 27 | 113 | 33 | 480 | 29455 | 71860 | 33
LTC10488 | 2003-10-23 | 18 | 3 | 2 | 16 | 72 | 38 | 468 | 29588 | 74565 | 21
LTC10488 | 2004-10-26 | 18 | 3 | 0 | 29 | 86 | 44 | 485 | 30086 | 75147 | 32
LTC10500 | 1993-09-23 | 0 | 0 | 0 | 3 | 0 | 23 | 404 | 32720 | 72550 | 3
LTC10500 | 1996-04-09 | 0 | 0 | 6 | 60 | 153 | 70 | 610 | 30994 | 71622 | 66
LTC10500 | 1996-12-16 | 2 | 0 | 0 | 20 | 0 | 70 | 680 | 27603 | 62907 | 20
LTC10500 | 1997-05-29 | 56 | 35 | 11 | 308 | 1890 | 70 | 690 | 30274 | 74140 | 354
LTC10500 | 1997-06-16 | 46 | 28 | 16 | 279 | 1612 | 66 | 698 | 29882 | 72779 | 323
LTC10500 | 1998-04-24 | 21 | 0 | 3 | 31 | 153 | 39 | 491 | 27036 | 71009 | 34
LTC10500 | 1999-04-12 | 22 | 13 | 16 | 55 | 148 | 34 | 708 | 28746 | 68207 | 84
LTC10500 | 2000-05-08 | 29 | 12 | 3 | 58 | 194 | 29 | 488 | 29264 | 68482 | 73
LTC10500 | 2001-10-11 | 38 | 24 | 5 | 76 | 441 | 25 | 453 | 29115 | 66609 | 105
LTC10500 | 2002-06-18 | 54 | 15 | 73 | 97 | 448 | 19 | 450 | 31378 | 70398 | 185
LTC10500 | 2003-06-16 | 16 | 11 | 78 | 65 | 220 | 29 | 407 | 29180 | 67299 | 154
LTC10500 | 2004-05-06 | 6 | 4 | 4 | 40 | 1 | 32 | 440 | 25643 | 63894 | 48
LTC10500 | 2005-06-22 | 7 | 0 | 3 | 16 | 53 | 23 | 406 | 31158 | 76306 | 19
LTC10501 | 1993-08-16 | 29 | 0 | 0 | 5 | 19 | 47 | 426 | 30521 | 77614 | 5
LTC10501 | 1994-06-07 | 15 | 0 | 0 | 5 | 21 | 42 | 348 | 29448 | 70558 | 5
LTC10501 | 1995-08-14 | 56 | 2 | 2 | 6 | 8 | 68 | 632 | 28630 | 74812 | 10
LTC10501 | 1995-10-04 | 14 | 2 | 0 | 12 | 35 | 9 | 374 | 39515 | 86809 | 14
LTC10501 | 1995-10-07 | 5 | 0 | 0 | 12 | 13 | 10 | 374 | 37093 | 72558 | 12
LTC10501 | 1996-06-03 | 0 | 0 | 1 | 0 | 0 | 0 | 210 | 28832 | 63186 | 1
LTC10501 | 1996-06-06 | 13 | 0 | 1 | 1 | 18 | 0 | 203 | 20588 | 45765 | 2
LTC10501 | 1997-05-23 | 29 | 7 | 6 | 13 | 125 | 0 | 421 | 31216 | 68386 | 26
LTC10501 | 1998-01-30 | 0 | 3 | 0 | 9 | 66 | 0 | 328 | 27204 | 61094 | 12
LTC10501 | 2000-07-03 | 6 | 0 | 0 | 0 | 3 | 12 | 319 | 27888 | 67767 | 0
LTC10501 | 2002-09-04 | 7 | 0 | 0 | 2 | 5 | 0 | 301 | 29562 | 67986 | 2
LTC10501 | 2003-08-04 | 9 | 0 | 0 | 0 | 8 | 12 | 312 | 30126 | 69552 | 0
LTC10501 | 2004-08-03 | 8 | 0 | 0 | 0 | 9 | 32 | 328 | 32457 | 77466 | 0
LTC10503 | 1993-09-02 | 145 | 0 | 0 | 11 | 89 | 103 | 630 | 25699 | 71226 | 11
LTC10503 | 1994-06-07 | 75 | 0 | 6 | 15 | 57 | 72 | 508 | 26620 | 70773 | 21
LTC10503 | 1995-08-10 | 73 | 5 | 0 | 14 | 77 | 75 | 561 | 27959 | 71534 | 19
LTC10503 | 1996-03-20 | 97 | 0 | 0 | 8 | 68 | 33 | 614 | 27814 | 67357 | 8
LTC10503 | 1997-05-27 | 54 | 4 | 2 | 11 | 30 | 46 | 633 | 24469 | 68580 | 17
LTC10503 | 1998-09-02 | 8 | 2 | 3 | 12 | 12 | 0 | 303 | 28292 | 69036 | 17
LTC10503 | 1999-08-15 | 7 | 0 | 0 | 0 | 0 | 0 | 399 | 27798 | 64177 | 0
LTC10503 | 2000-10-31 | 4 | 0 | 0 | 0 | 0 | 0 | 416 | 27470 | 62351 | 0
LTC10503 | 2001-10-24 | 5 | 5 | 0 | 8 | 25 | 27 | 349 | 12391 | 48136 | 13
LTC10503 | 2002-11-26 | 5 | 0 | 0 | 1 | 0 | 0 | 359 | 28370 | 66829 | 1
LTC10503 | 2003-12-01 | 8 | 0 | 0 | 4 | 19 | 36 | 397 | 24378 | 72746 | 4
LTC10503 | 2004-10-20 | 7 | 0 | 0 | 3 | 24 | 5 | 313 | 31064 | 69965 | 3
LTC10535 | 1993-08-16 | 38 | 0 | 6 | 5 | 26 | 119 | 623 | 23995 | 73463 | 11
LTC10535 | 1994-06-03 | 25 | 0 | 2 | 1 | 0 | 91 | 525 | 23986 | 70058 | 3
LTC10535 | 1994-07-07 | 21 | 0 | 3 | 2 | 0 | 88 | 573 | 20224 | 69817 | 5
LTC10535 | 1994-08-03 | 32 | 0 | 0 | 0 | 0 | 131 | 628 | 23852 | 68043 | 0
LTC10535 | 1995-08-16 | 99 | 2 | 0 | 11 | 45 | 212 | 913 | 23010 | 70364 | 13
LTC10535 | 1996-04-16 | 32 | 0 | 0 | 4 | 21 | 31 | 484 | 30279 | 69613 | 4
LTC10535 | 1996-04-19 | 43 | 0 | 0 | 7 | 36 | 38 | 499 | 29645 | 67421 | 7
LTC10535 | 1997-05-20 | 48 | 0 | 0 | 7 | 23 | 97 | 683 | 22567 | 72161 | 7
LTC10535 | 1998-07-07 | 88 | 3 | 0 | 4 | 22 | 206 | 890 | 10963 | 70578 | 7
LTC10535 | 1999-07-28 | 105 | 0 | 0 | 0 | 14 | 228 | 837 | 18465 | 64716 | 0
LTC10535 | 1999-10-07 | 8 | 0 | 0 | 0 | 0 | 0 | 292 | 24920 | 68188 | 0
LTC10535 | 2000-07-03 | 33 | 0 | 0 | 0 | 4 | 10 | 312 | 28144 | 70469 | 0
LTC10535 | 2002-01-29 | 0 | 0 | 0 | 0 | 8 | 0 | 282 | 23736 | 52772 | 0
LTC10535 | 2002-08-28 | 10 | 0 | 0 | 3 | 13 | 0 | 302 | 27849 | 66563 | 3
LTC10535 | 2003-08-07 | 7 | 0 | 0 | 0 | 14 | 0 | 305 | 28065 | 64609 | 0
LTC10535 | 2004-07-26 | 8 | 0 | 0 | 0 | 8 | 0 | 277 | 30441 | 70544 | 0
LTC10535 | 2005-07-25 | 26 | 0 | 0 | 2 | 12 | 40 | 390 | 22269 | 72522 | 2
LTC10541 | 1993-08-13 | 69 | 0 | 3 | 9 | 50 | 108 | 680 | 25034 | 68438 | 12
LTC10541 | 1994-05-26 | 69 | 0 | 0 | 8 | 37 | 200 | 657 | 26500 | 70760 | 8
LTC10541 | 1994-06-23 | 65 | 0 | 0 | 9 | 53 | 129 | 747 | 23400 | 67224 | 9
LTC10541 | 1994-07-26 | 57 | 0 | 3 | 9 | 60 | 135 | 700 | 25494 | 66554 | 12
LTC10541 | 1994-08-24 | 32 | 0 | 0 | 3 | 10 | 77 | 210 | 26687 | 73999 | 3
LTC10541 | 1995-08-10 | 62 | 3 | 0 | 6 | 47 | 151 | 823 | 25937 | 72068 | 9
LTC10541 | 1996-03-05 | 16 | 2 | 2 | 7 | 53 | 47 | 682 | 28672 | 67293 | 11
LTC10541 | 1997-05-21 | 48 | 5 | 1 | 8 | 42 | 67 | 642 | 27841 | 69027 | 14
LTC10541 | 1998-01-22 | 19 | 0 | 0 | 2 | 22 | 32 | 488 | 24776 | 66117 | 2
LTC10541 | 1999-02-25 | 22 | 6 | 0 | 4 | 36 | 0 | 450 | 30200 | 72064 | 10
LTC10541 | 2000-01-18 | 34 | 5 | 0 | 10 | 77 | 18 | 396 | 28841 | 66551 | 15
LTC10541 | 2003-11-21 | 17 | 3 | 0 | 6 | 36 | 6 | 341 | 31535 | 70307 | 9
LTC10541 | 2004-12-01 | 10 | 4 | 0 | 5 | 32 | 12 | 370 | 29482 | 65542 | 9
LTC10541 | 2005-08-01 | 13 | 0 | 0 | 8 | 36 | 13 | 363 | 31260 | 74890 | 8
LTC10544 | 1993-08-16 | 57 | 0 | 0 | 10 | 13 | 122 | 624 | 25473 | 69843 | 10
LTC10544 | 1994-06-03 | 14 | 0 | 0 | 2 | 4 | 87 | 515 | 22996 | 68380 | 2
LTC10544 | 1994-07-07 | 19 | 0 | 0 | 3 | 24 | 95 | 619 | 28819 | 73011 | 3
LTC10544 | 1994-08-03 | 28 | 0 | 0 | 0 | 18 | 203 | 552 | 26696 | 69615 | 0
LTC10544 | 1995-08-16 | 64 | 3 | 0 | 11 | 25 | 224 | 1050 | 21049 | 67505 | 14
LTC10544 | 1996-04-12 | 17 | 0 | 1 | 2 | 36 | 45 | 6885 | 27469 | 67418 | 3
LTC10544 | 1997-05-20 | 21 | 0 | 0 | 0 | 1 | 79 | 663 | 24447 | 69818 | 0
LTC10544 | 1998-07-07 | 45 | 0 | 0 | 3 | 16 | 118 | 718 | 19108 | 70497 | 3
LTC10544 | 1999-07-28 | 10 | 0 | 0 | 0 | 1 | 6 | 520 | 24732 | 60945 | 0
LTC10544 | 2000-07-03 | 6 | 0 | 0 | 0 | 0 | 10 | 379 | 28843 | 71886 | 0
LTC10544 | 2002-01-29 | 4 | 0 | 0 | 2 | 0 | 0 | 334 | 27305 | 62644 | 2
LTC10544 | 2002-08-28 | 6 | 0 | 0 | 2 | 11 | 11 | 290 | 28076 | 66740 | 2
LTC10544 | 2003-08-07 | 7 | 0 | 0 | 3 | 11 | 14 | 315 | 29003 | 68019 | 3
LTC10544 | 2004-07-26 | 4 | 0 | 0 | 0 | 0 | 2 | 265 | 30128 | 69742 | 0
LTC10544 | 2005-07-25 | 11 | 0 | 0 | 3 | 18 | 10 | 325 | 27697 | 69282 | 3
LTC10558 | 1993-09-30 | 20 | 0 | 1 | 14 | 41 | 0 | 455 | 34230 | 70650 | 15
LTC10558 | 1994-06-20 | 55 | 0 | 0 | 7 | 54 | 121 | 751 | 24411 | 72703 | 7
LTC10558 | 1996-03-25 | 117 | 9 | 0 | 8 | 80 | 50 | 568 | 31833 | 70543 | 17
LTC10558 | 1997-05-21 | 60 | 0 | 0 | 6 | 46 | 66 | 653 | 24775 | 71662 | 6
LTC10558 | 1998-12-09 | 6 | 1 | 3 | 0 | 7 | 0 | 325 | 26553 | 60239 | 4
LTC10558 | 1999-09-09 | 12 | 2 | 0 | 4 | 24 | 0 | 335 | 30701 | 70711 | 6
LTC10558 | 2000-09-20 | 11 | 0 | 0 | 7 | 13 | 0 | 355 | 27761 | 63852 | 7
LTC10558 | 2002-10-16 | 9 | 0 | 1 | 4 | 11 | 60 | 354 | 30673 | 70269 | 5
LTC10558 | 2003-09-23 | 10 | 0 | 1 | 2 | 2 | 0 | 297 | 29916 | 67930 | 3
LTC10558 | 2004-09-09 | 7 | 0 | 0 | 0 | 0 | 17 | 306 | 41545 | 96651 | 0
LTC10562 | 1993-08-13 | 93 | 0 | 0 | 8 | 68 | 91 | 723 | 24258 | 75620 | 8
LTC10562 | 1994-05-26 | 86 | 0 | 0 | 6 | 36 | 66 | 519 | 27282 | 68779 | 6
LTC10562 | 1994-06-23 | 68 | 0 | 3 | 8 | 43 | 82 | 675 | 26043 | 69369 | 11
LTC10562 | 1994-07-26 | 58 | 0 | 0 | 4 | 36 | 76 | 608 | 25124 | 64996 | 4
LTC10562 | 1994-08-24 | 47 | 0 | 0 | 4 | 42 | 40 | 566 | 27743 | 69289 | 4
LTC10562 | 1995-08-15 | 72 | 1 | 0 | 7 | 27 | 87 | 710 | 24671 | 68695 | 8
LTC10562 | 1996-03-04 | 27 | 0 | 4 | 2 | 12 | 36 | 611 | 28273 | 66749 | 6
LTC10562 | 1997-05-21 | 47 | 0 | 0 | 3 | 16 | 48 | 618 | 26204 | 67213 | 3
LTC10562 | 1998-03-16 | 10 | 0 | 0 | 0 | 0 | 5 | 417 | 29091 | 69716 | 0
LTC10562 | 1999-04-13 | 50 | 2 | 0 | 2 | 21 | 52 | 540 | 24752 | 71111 | 4
LTC10562 | 2000-03-31 | 47 | 0 | 0 | 4 | 36 | 40 | 493 | 26683 | 70682 | 4
LTC10562 | 2001-05-24 | 47 | 2 | 2 | 4 | 38 | 80 | 574 | 19719 | 66178 | 8
LTC10562 | 2002-05-17 | 77 | 22 | 10 | 4 | 29 | 90 | 681 | 24875 | 69914 | 36
LTC10562 | 2003-05-29 | 86 | 0 | 0 | 5 | 42 | 72 | 739 | 19849 | 68932 | 5
LTC10562 | 2004-05-05 | 19 | 4 | 6 | 26 | 36 | 4 | 403 | 29764 | 67535 | 36
LTC10562 | 2005-05-10 | 10 | 0 | 0 | 3 | 12 | 0 | 339 | 30309 | 68320 | 3
LTC10653 | 1993-09-27 | 27 | 0 | 0 | 0 | 0 | 32 | 449 | 25833 | 67605 | 0
LTC10653 | 1994-07-19 | 39 | 0 | 7 | 3 | 0 | 58 | 599 | 21868 | 70836 | 10
LTC10653 | 1996-03-14 | 264 | 33 | 12 | 42 | 259 | 40 | 610 | 19660 | 67502 | 87
LTC10653 | 1997-05-20 | 137 | 14 | 0 | 25 | 191 | 40 | 712 | 14027 | 69197 | 39
LTC10653 | 1998-02-04 | 103 | 19 | 11 | 28 | 202 | 19 | 451 | 26071 | 70261 | 58
LTC10653 | 1999-01-27 | 151 | 14 | 3 | 22 | 150 | 74 | 658 | 15238 | 62884 | 39
LTC10653 | 2000-02-28 | 16 | 2 | 0 | 6 | 37 | 0 | 338 | 29421 | 68568 | 8
LTC10653 | 2001-03-14 | 17 | 2 | 0 | 9 | 41 | 14 | 400 | 30323 | 69891 | 11
LTC10653 | 2002-01-22 | 16 | 3 | 0 | 19 | 52 | 22 | 380 | 31119 | 66444 | 22
LTC10653 | 2003-03-06 | 14 | 0 | 0 | 7 | 32 | 0 | 398 | 26507 | 62172 | 7
LTC10653 | 2004-02-19 | 15 | 0 | 0 | 5 | 22 | 24 | 445 | 28464 | 84697 | 5
LTC10653 | 2005-02-23 | 11 | 0 | 1 | 5 | 20 | 22 | 539 | 29361 | 68424 | 6
LTC10656 | 1993-08-17 | 66 | 0 | 4 | 16 | 74 | 88 | 648 | 25010 | 69304 | 20
LTC10656 | 1994-05-25 | 93 | 0 | 0 | 5 | 29 | 175 | 836 | 8163 | 67613 | 5
LTC10656 | 1994-06-23 | 64 | 0 | 5 | 15 | 58 | 100 | 560 | 30117 | 75098 | 20
LTC10656 | 1994-07-26 | 50 | 0 | 0 | 10 | 71 | 95 | 633 | 28607 | 70667 | 10
LTC10656 | 1994-08-24 | 44 | 0 | 0 | 10 | 62 | 62 | 522 | 28311 | 67726 | 10
LTC10656 | 1995-08-10 | 85 | 3 | 0 | 13 | 59 | 170 | 906 | 23571 | 67896 | 16
LTC10656 | 1996-02-29 | 26 | 1 | 0 | 6 | 30 | 88 | 683 | 22161 | 64336 | 7
LTC10656 | 1997-05-21 | 55 | 5 | 3 | 17 | 68 | 124 | 783 | 18421 | 66544 | 25
LTC10656 | 1998-08-24 | 120 | 7 | 1 | 9 | 50 | 208 | 939 | 15118 | 65422 | 17
LTC10656 | 2000-08-02 | 61 | 4 | 0 | 7 | 45 | 106 | 603 | 23090 | 68126 | 11
LTC10656 | 2002-10-04 | 82 | 6 | 2 | 11 | 49 | 186 | 868 | 18044 | 63723 | 19
LTC10656 | 2003-09-02 | 131 | 0 | 0 | 13 | 86 | 235 | 802 | 20889 | 71787 | 13
LTC10656 | 2003-12-16 | 28 | 0 | 0 | 8 | 57 | 39 | 430 | 24961 | 69221 | 8
LTC10660 | 1997-05-20 | 36 | 0 | 0 | 20 | 75 | 0 | 353 | 31889 | 69770 | 20
LTC10660 | 1998-04-01 | 20 | 1 | 0 | 8 | 40 | 0 | 308 | 27252 | 65192 | 9
LTC10660 | 1999-05-27 | 12 | 3 | 0 | 6 | 28 | 0 | 374 | 27066 | 68062 | 9
LTC10660 | 2000-04-13 | 11 | 0 | 0 | 0 | 3 | 19 | 297 | 28887 | 71216 | 0
LTC10660 | 2001-05-03 | 21 | 0 | 0 | 6 | 32 | 19 | 344 | 27967 | 68967 | 6
LTC10660 | 2002-03-20 | 16 | 2 | 0 | 4 | 21 | 26 | 446 | 25910 | 68195 | 6
LTC10660 | 2002-05-02 | 21 | 2 | 0 | 6 | 32 | 26 | 332 | 25946 | 67512 | 8
LTC10660 | 2003-05-14 | 15 | 1 | 0 | 4 | 1 | 48 | 368 | 25586 | 67669 | 5
LTC10660 | 2004-04-15 | 168 | 21 | 4 | 69 | 460 | 102 | 481 | 24088 | 69116 | 94
LTC10660 | 2005-03-03 | 4 | 2 | 0 | 0 | 0 | 10 | 312 | 28517 | 66538 | 2
LTC10660 | 2006-04-04 | 2 | 10 | 18 | 62 | 5 | 10 | 341 | 20765 | 55377 | 90
LTC10662 | 1993-08-16 | 81 | 0 | 7 | 42 | 82 | 165 | 757 | 23222 | 70868 | 49
LTC10662 | 1994-06-03 | 42 | 0 | 2 | 9 | 43 | 88 | 452 | 27830 | 67614 | 11
LTC10662 | 1994-07-07 | 42 | 0 | 0 | 13 | 84 | 101 | 686 | 29269 | 72434 | 13
LTC10662 | 1994-08-03 | 125 | 0 | 15 | 19 | 151 | 124 | 726 | 26934 | 70021 | 34
LTC10662 | 1995-08-21 | 92 | 8 | 0 | 12 | 95 | 249 | 1140 | 22470 | 69858 | 20
LTC10662 | 1996-04-11 | 116 | 0 | 0 | 11 | 70 | 54 | 592 | 28241 | 72110 | 11
LTC10662 | 1997-05-20 | 79 | 0 | 0 | 8 | 67 | 124 | 763 | 24603 | 68120 | 8
LTC10662 | 1998-06-11 | 85 | 5 | 2 | 10 | 52 | 179 | 859 | 13810 | 65469 | 17
LTC10662 | 1999-07-06 | 91 | 3 | 0 | 7 | 45 | 23 | 772 | 20760 | 71502 | 10
LTC10662 | 2000-07-03 | 86 | 3 | 0 | 6 | 40 | 223 | 834 | 19238 | 73250 | 9
LTC10662 | 2001-06-18 | 69 | 2 | 0 | 7 | 29 | 141 | 688 | 21246 | 73082 | 9
LTC10662 | 2002-06-24 | 18 | 0 | 0 | 0 | 6 | 2 | 349 | 20342 | 68157 | 0
LTC10662 | 2003-08-07 | 123 | 0 | 0 | 0 | 9 | 55 | 556 | 16187 | 67908 | 0
LTC10662 | 2004-10-29 | 5 | 2 | 1 | 1 | 0 | 12 | 488 | 11018 | 80537 | 4
LTC10662 | 2005-05-26 | 8 | 0 | 0 | 2 | 9 | 14 | 337 | 25275 | 71636 | 2
LTC10663 | 1993-08-16 | 129 | 0 | 3 | 6 | 40 | 211 | 876 | 21476 | 73589 | 9
LTC10663 | 1994-06-07 | 52 | 0 | 0 | 5 | 35 | 86 | 465 | 29373 | 69944 | 5
LTC10663 | 1995-08-16 | 128 | 0 | 0 | 6 | 46 | 213 | 1008 | 19244 | 69394 | 6
LTC10663 | 1996-04-11 | 35 | 0 | 3 | 4 | 26 | 29 | 535 | 30462 | 72858 | 7
LTC10663 | 1997-05-20 | 75 | 4 | 3 | 31 | 29 | 179 | 872 | 15600 | 68371 | 38
LTC10663 | 1998-06-11 | 78 | 4 | 0 | 8 | 41 | 171 | 834 | 16716 | 66637 | 12
LTC10663 | 1999-07-07 | 8 | 0 | 1 | 0 | 1 | 0 | 302 | 29813 | 72394 | 1
LTC10663 | 2000-07-03 | 5 | 0 | 0 | 0 | 0 | 17 | 394 | 26907 | 72176 | 0
LTC10663 | 2001-06-18 | 6 | 0 | 0 | 0 | 0 | 0 | 416 | 28748 | 67313 | 0
LTC10663 | 2002-06-24 | 13 | 0 | 0 | 0 | 4 | 0 | 290 | 30221 | 70941 | 0
LTC10663 | 2005-04-21 | 5 | 0 | 2 | 6 | 0 | 52 | 264 | 8508 | 47670 | 8
LTC10663 | 2005-06-17 | 0 | 0 | 0 | 3 | 0 | 24 | 353 | 26304 | 69366 | 3
LTC10669 | 1993-09-03 | 116 | 0 | 0 | 13 | 95 | 169 | 768 | 25864 | 76864 | 13
LTC10669 | 1994-05-13 | 57 | 0 | 0 | 5 | 30 | 80 | 570 | 27148 | 69307 | 5
LTC10669 | 1996-03-26 | 24 | 258 | 75 | 274 | 16 | 175 | 806 | 19490 | 66945 | 607
LTC10669 | 1996-06-07 | 42 | 0 | 3 | 20 | 51 | 112 | 614 | 26725 | 70014 | 23
LTC10669 | 1997-07-09 | 128 | 126 | 40 | 293 | 72 | 325 | 870 | 18388 | 68579 | 459
LTC10669 | 1998-11-20 | 39 | 5 | 7 | 4 | 29 | 53 | 552 | 20748 | 60691 | 16
LTC10669 | 1999-09-08 | 125 | 3 | 0 | 6 | 29 | 286 | 1108 | 9012 | 67639 | 9
LTC10669 | 2000-09-15 | 56 | 0 | 0 | 0 | 5 | 78 | 713 | 16296 | 62629 | 0
LTC10669 | 2001-11-05 | 37 | 1 | 0 | 2 | 7 | 95 | 841 | 13326 | 51069 | 3
LTC10669 | 2002-10-16 | 20 | 0 | 0 | 2 | 10 | 55 | 478 | 27225 | 67327 | 2
LTC10669 | 2003-09-23 | 17 | 0 | 0 | 1 | 1 | 43 | 436 | 26212 | 64305 | 1
LTC10669 | 2004-08-26 | 42 | 0 | 0 | 1 | 0 | 45 | 486 | 26939 | 67910 | 1
LTC10669 | 2005-10-05 | 5 | 1 | 0 | 2 | 47 | 18 | 687 | 613 | 1222 | 3
LTC11028 | 1993-08-17 | 127 | 0 | 0 | 9 | 6 | 119 | 750 | 20004 | 68489 | 9
LTC11625 | 1993-09-07 | 52 | 0 | 6 | 57 | 259 | 45 | 594 | 32096 | 70610 | 63
LTC11625 | 1993-10-12 | 80 | 0 | 5 | 58 | 269 | 84 | 609 | 30543 | 74066 | 63
LTC11625 | 1994-06-14 | 29 | 0 | 0 | 32 | 151 | 63 | 617 | 31307 | 75002 | 32
LTC11625 | 1996-04-08 | 36 | 6 | 2 | 29 | 130 | 51 | 641 | 27708 | 68358 | 37
LTC11625 | 1997-05-29 | 28 | 4 | 0 | 25 | 148 | 51 | 674 | 32108 | 75232 | 29
LTC11625 | 1998-09-01 | 28 | 10 | 26 | 28 | 129 | 0 | 471 | 29105 | 66361 | 64
LTC11625 | 1999-09-08 | 24 | 11 | 4 | 49 | 158 | 18 | 448 | 28539 | 66939 | 64
LTC11625 | 2000-08-28 | 46 | 11 | 4 | 49 | 179 | 0 | 460 | 28559 | 64125 | 64
LTC11625 | 2001-11-01 | 47 | 52 | 26 | 216 | 553 | 67 | 634 | 11136 | 38833 | 294
LTC11625 | 2002-10-10 | 4 | 3 | 4 | 29 | 13 | 0 | 489 | 32251 | 71815 | 36
LTC11625 | 2003-09-16 | 62 | 8 | 4 | 41 | 120 | 28 | 505 | 27777 | 68422 | 53
LTC11625 | 2004-09-21 | 134 | 41 | 8 | 138 | 793 | 21 | 514 | 31677 | 74161 | 187
LTC11625 | 2005-01-05 | 136 | 59 | 12 | 222 | 1328 | 141 | 566 | 30543 | 67185 | 293
LTC11628 | 1993-09-10 | 27 | 0 | 0 | 10 | 57 | 77 | 497 | 27868 | 69985 | 10
LTC11628 | 1994-06-10 | 17 | 0 | 0 | 4 | 17 | 152 | 818 | 7817 | 74307 | 4
LTC11628 | 1996-04-23 | 7 | 0 | 0 | 3 | 11 | 29 | 409 | 28120 | 70710 | 3
LTC11628 | 1997-05-16 | 20 | 2 | 0 | 3 | 0 | 62 | 634 | 18459 | 67931 | 5
LTC11628 | 1998-08-31 | 17 | 3 | 0 | 0 | 21 | 71 | 488 | 18489 | 57666 | 3
LTC11628 | 1999-09-13 | 15 | 2 | 0 | 2 | 14 | 68 | 492 | 22846 | 68844 | 4
LTC11628 | 2000-10-10 | 17 | 0 | 0 | 4 | 16 | 84 | 519 | 16649 | 68687 | 4
LTC11628 | 2001-10-10 | 8 | 6 | 0 | 8 | 12 | 18 | 485 | 20432 | 65859 | 14
LTC11628 | 2002-11-01 | 6 | 4 | 0 | 2 | 2 | 66 | 407 | 29731 | 71507 | 6
LTC11628 | 2003-09-29 | 3 | 3 | 0 | 0 | 0 | 8 | 305 | 29100 | 67212 | 3
LTC11628 | 2004-09-22 | 0 | 0 | 0 | 0 | 0 | 12 | 345 | 28701 | 66990 | 0
LTC11629 | 1993-09-10 | 45 | 0 | 7 | 45 | 2239 | 184 | 1781 | 14200 | 78221 | 52
LTC11629 | 1994-06-10 | 37 | 0 | 13 | 36 | 181 | 68 | 1064 | 21663 | 74046 | 49
LTC11629 | 1996-04-23 | 42 | 11 | 6 | 38 | 200 | 151 | 1119 | 17553 | 67608 | 55
LTC11629 | 1998-08-31 | 74 | 23 | 2 | 28 | 158 | 189 | 1580 | 20234 | 68238 | 53
LTC11629 | 1999-09-13 | 56 | 12 | 0 | 30 | 271 | 174 | 1647 | 18681 | 67067 | 42
LTC11629 | 2000-10-10 | 1466 | 17070 | 12552 | 42577 | 630 | 289 | 2613 | 7759 | 61623 | 72199
LTC11629 | 2001-10-10 | 19 | 26 | 17 | 110 | 359 | 30 | 850 | 18305 | 56328 | 153
LTC11629 | 2002-11-01 | 50 | 12 | 6 | 44 | 194 | 0 | 596 | 29710 | 71251 | 62
LTC11629 | 2003-09-29 | 26 | 8 | 4 | 40 | 161 | 26 | 588 | 29339 | 67811 | 52
LTC11629 | 2004-09-22 | 22 | 9 | 2 | 36 | 146 | 20 | 559 | 27172 | 62905 | 47
LTC11630 | 1993-09-27 | 30 | 0 | 0 | 7 | 25 | 0 | 415 | 33713 | 73626 | 7
LTC11630 | 1994-06-06 | 22 | 0 | 0 | 4 | 45 | 50 | 368 | 31896 | 72261 | 4
LTC11630 | 1996-04-23 | 29 | 0 | 0 | 6 | 35 | 102 | 514 | 28758 | 73742 | 6
LTC11630 | 1997-05-20 | 17 | 0 | 0 | 8 | 39 | 23 | 489 | 29454 | 64587 | 8
LTC11630 | 1998-04-28 | 12 | 0 | 0 | 5 | 27 | 41 | 371 | 32630 | 77415 | 5
LTC11630 | 1999-05-26 | 15 | 2 | 0 | 4 | 30 | 37 | 424 | 27928 | 71596 | 6
LTC11630 | 2000-04-28 | 6 | 0 | 0 | 0 | 8 | 7 | 362 | 29939 | 66451 | 0
LTC11630 | 2001-06-21 | 5 | 0 | 0 | 2 | 6 | 32 | 389 | 28848 | 69542 | 2
LTC11630 | 2002-07-19 | 5 | 0 | 2 | 0 | 8 | 9 | 323 | 28901 | 67308 | 2
LTC11630 | 2003-07-09 | 6 | 0 | 0 | 3 | 22 | 17 | 357 | 27516 | 65444 | 3
LTC11630 | 2004-06-22 | 5 | 0 | 0 | 0 | 8 | 0 | 450 | 28963 | 68169 | 0
LTC11630 | 2005-06-27 | 0 | 0 | 0 | 0 | 4 | 0 | 390 | 32732 | 70330 | 0
LTC11631 | 1993-09-27 | 19 | 0 | 1 | 11 | 47 | 38 | 364 | 33781 | 74834 | 12
LTC11631 | 1994-06-06 | 17 | 0 | 0 | 7 | 45 | 68 | 371 | 28962 | 74051 | 7
LTC11631 | 1996-04-23 | 40 | 0 | 2 | 8 | 50 | 50 | 628 | 32325 | 72040 | 10
LTC11631 | 1997-05-20 | 19 | 0 | 0 | 7 | 47 | 0 | 410 | 33698 | 70272 | 7
LTC11631 | 1998-04-28 | 11 | 0 | 0 | 0 | 26 | 35 | 422 | 30375 | 71594 | 0
LTC11631 | 1999-06-22 | 17 | 0 | 0 | 5 | 24 | 80 | 610 | 29126 | 78183 | 5
LTC11631 | 2000-05-30 | 4 | 0 | 0 | 0 | 0 | 14 | 394 | 27793 | 65725 | 0
LTC11631 | 2002-09-05 | 5 | 0 | 0 | 1 | 8 | 28 | 401 | 28017 | 70144 | 1
LTC11631 | 2003-07-09 | 3 | 0 | 0 | 2 | 6 | 11 | 340 | 29928 | 69530 | 2
LTC11631 | 2004-06-22 | 5 | 0 | 0 | 0 | 4 | 6 | 374 | 28824 | 69464 | 0
LTC11631 | 2005-06-26 | 7 | 0 | 0 | 2 | 8 | 0 | 300 | 29802 | 66496 | 2
LTC11820 | 1993-08-13 | 11 | 0 | 0 | 9 | 58 | 32 | 407 | 32389 | 74473 | 9
LTC11820 | 1994-06-07 | 18 | 0 | 0 | 8 | 49 | 33 | 333 | 32702 | 68003 | 8
LTC11820 | 1995-08-16 | 19 | 2 | 0 | 8 | 48 | 42 | 416 | 32791 | 70314 | 10
LTC11820 | 1996-03-20 | 21 | 1 | 0 | 5 | 38 | 29 | 604 | 32212 | 69444 | 6
LTC11820 | 1997-05-27 | 16 | 4 | 4 | 29 | 44 | 17 | 513 | 31336 | 70615 | 37
LTC11820 | 1998-03-27 | 10 | 0 | 0 | 4 | 37 | 28 | 391 | 26165 | 65050 | 4
LTC11820 | 1999-07-22 | 7 | 0 | 0 | 0 | 14 | 7 | 295 | 28219 | 69712 | 0
LTC11820 | 2000-04-19 | 6 | 0 | 0 | 3 | 6 | 49 | 382 | 23727 | 69418 | 3
LTC11820 | 2001-10-10 | 3 | 6 | 0 | 6 | 5 | 17 | 564 | 51012 | 277817 | 12
LTC11820 | 2002-05-14 | 5 | 0 | 0 | 4 | 14 | 34 | 378 | 29978 | 73848 | 4
LTC11820 | 2003-09-12 | 5 | 0 | 1 | 6 | 20 | 20 | 448 | 29158 | 69304 | 7
LTC11820 | 2004-07-27 | 10 | 1 | 0 | 5 | 22 | 25 | 333 | 28409 | 66886 | 6
LTC11820 | 2005-05-11 | 6 | 0 | 0 | 4 | 12 | 15 | 328 | 29242 | 68153 | 4
LTC11822 | 1993-09-27 | 20 | 0 | 0 | 12 | 86 | 41 | 396 | 33886 | 71525 | 12
LTC11822 | 1994-06-06 | 19 | 0 | 0 | 6 | 32 | 39 | 326 | 32143 | 77836 | 6
LTC11822 | 1996-05-01 | 31 | 0 | 1 | 9 | 45 | 67 | 469 | 28374 | 67346 | 10
LTC11822 | 1997-05-20 | 25 | 0 | 0 | 5 | 43 | 16 | 468 | 31530 | 72347 | 5
LTC11822 | 1998-02-10 | 23 | 2 | 0 | 6 | 73 | 52 | 489 | 28677 | 72278 | 8
LTC11822 | 1999-03-18 | 31 | 2 | 0 | 5 | 43 | 120 | 509 | 23242 | 71204 | 7
LTC11822 | 2000-03-14 | 5 | 0 | 0 | 0 | 8 | 0 | 347 | 28057 | 62625 | 0
LTC11822 | 2001-04-17 | 9 | 0 | 0 | 1 | 21 | 8 | 330 | 30498 | 68288 | 1
LTC11822 | 2003-02-18 | 5 | 0 | 0 | 3 | 7 | 0 | 389 | 28498 | 65212 | 3
LTC11822 | 2004-01-28 | 5 | 0 | 0 | 2 | 1 | 29 | 385 | 25869 | 62648 | 2
LTC11822 | 2005-02-04 | 6 | 0 | 0 | 0 | 0 | 20 | 442 | 29694 | 65144 | 0
LTC11833 | 1993-09-13 | 18 | 0 | 0 | 7 | 37 | 74 | 460 | 28422 | 69582 | 7
LTC11833 | 1996-04-03 | 14 | 0 | 1 | 2 | 12 | 40 | 479 | 30305 | 67350 | 3
LTC11833 | 1997-06-03 | 16 | 0 | 2 | 13 | 39 | 65 | 540 | 26937 | 67434 | 15
LTC11833 | 1998-10-23 | 12 | 2 | 0 | 4 | 19 | 33 | 379 | 22496 | 59540 | 6
LTC11833 | 2000-12-07 | 17 | 0 | 0 | 2 | 24 | 40 | 520 | 23852 | 62661 | 2
LTC11833 | 2001-11-21 | 18 | 4 | 0 | 2 | 12 | 60 | 479 | 17305 | 51629 | 6
LTC11833 | 2002-12-03 | 17 | 0 | 0 | 2 | 18 | 0 | 522 | 22654 | 69650 | 2
LTC11833 | 2004-12-01 | 17 | 3 | 0 | 5 | 23 | 74 | 649 | 22813 | 69652 | 8
LTC11847 | 1993-09-02 | 48 | 0 | 6 | 12 | 52 | 45 | 343 | 32583 | 70683 | 18
LTC11847 | 1994-06-07 | 36 | 0 | 0 | 6 | 43 | 32 | 325 | 31453 | 66253 | 6
LTC11847 | 1995-08-16 | 38 | 5 | 0 | 18 | 104 | 39 | 421 | 31513 | 70384 | 23
LTC11847 | 1996-03-20 | 26 | 0 | 8 | 20 | 51 | 20 | 569 | 34677 | 68993 | 28
LTC11847 | 1997-02-26 | 0 | 0 | 0 | 0 | 0 | 0 | 268 | 23798 | 51034 | 0
LTC11847 | 1997-03-03 | 30 | 0 | 0 | 3 | 11 | 0 | 324 | 28326 | 59216 | 3
LTC11889 | 1993-08-13 | 41 | 0 | 0 | 11 | 56 | 31 | 412 | 34092 | 77150 | 11
LTC11889 | 1994-06-07 | 23 | 0 | 0 | 15 | 43 |  | 316 | 28296 | 66106 | 15
LTC11889 | 1995-08-16 | 30 | 2 | 0 | 6 | 58 | 37 | 407 | 32033 | 73067 | 8
LTC11889 | 1996-03-20 | 40 | 3 | 0 | 11 | 56 | 15 | 451 | 33876 | 70400 | 14
LTC11889 | 1997-05-23 | 21 | 2 | 0 | 4 | 50 | 0 | 417 | 33236 | 71036 | 6
LTC11889 | 1998-01-09 | 15 | 0 | 0 | 13 | 50 | 66 | 376 | 39590 | 78725 | 13
LTC11889 | 1999-03-19 | 15 | 4 | 3 | 4 | 34 | 81 | 492 | 24263 | 71027 | 11
LTC11889 | 2000-06-29 | 6 | 0 | 0 | 0 | 6 | 0 | 295 | 29874 | 69327 | 0
LTC11889 | 2001-04-03 | 5 | 0 | 1 | 4 | 13 | 10 | 352 | 29152 | 64493 | 5
LTC11889 | 2002-09-17 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 25935 | 66650 | 0
LTC11889 | 2003-04-02 | 8 | 0 | 0 | 4 | 12 | 0 | 370 | 28870 | 65062 | 4
LTC11889 | 2004-03-11 | 7 | 0 | 0 | 3 | 8 | 20 | 385 | 26840 | 61248 | 3
LTC11889 | 2006-03-22 | 7 | 5 | 0 | 7 | 7 | 40 | 552 | 20057 | 57018 | 12
LTC11889 | 2006-04-13 | 1 | 4 | 1 | 23 | 1 | 7 | 515 | 24405 | 62021 | 28
LTC11920 | 1993-09-13 | 59 | 0 | 0 | 14 | 66 | 47 | 539 | 26834 | 66295 | 14
LTC11920 | 1994-06-01 | 67 | 0 | 0 | 6 | 45 | 46 | 453 | 28194 | 72023 | 6
LTC11920 | 1996-04-03 | 261 | 0 | 3 | 6 | 45 | 78 | 723 | 17163 | 64716 | 9
LTC11920 | 1997-06-03 | 86 | 0 | 3 | 3 | 30 | 166 | 886 | 11825 | 67227 | 6
LTC11920 | 1998-10-23 | 80 | 5 | 1 | 7 | 49 | 165 | 913 | 6751 | 65213 | 13
LTC11920 | 1999-12-16 | 56 | 3 | 0 | 5 | 31 | 120 | 831 | 7674 | 73271 | 8
LTC11920 | 2000-12-07 | 102 | 2 | 0 | 5 | 40 | 62 | 690 | 21331 | 63458 | 7
LTC11920 | 2001-11-21 | 65 | 2 | 0 | 3 | 20 | 84 | 643 | 16130 | 53892 | 5
LTC11920 | 2002-12-13 | 44 | 0 | 0 | 3 | 25 | 51 | 564 | 23399 | 65353 | 3
LTC11920 | 2003-11-13 | 59 | 5 | 0 | 13 | 36 | 119 | 705 | 19728 | 75266 | 18
LTC11920 | 2004-12-01 | 33 | 2 | 0 | 3 | 28 | 36 | 514 | 28390 | 71599 | 5
LTC12000 | 1993-09-03 | 193 | 0 | 2 | 42 | 180 | 80 | 392 | 34607 | 72706 | 44
LTC12000 | 1994-05-13 | 33 | 0 | 0 | 12 | 58 | 125 | 540 | 25312 | 70254 | 12
LTC12000 | 1996-04-03 | 25 | 0 | 0 | 12 | 63 | 29 | 466 | 33505 | 71004 | 12
LTC12000 | 1997-06-10 | 40 | 2 | 2 | 13 | 66 | 140 | 524 | 27237 | 68998 | 17
LTC12000 | 1998-07-23 | 66 | 9 | 3 | 17 | 90 | 288 | 677 | 15933 | 76734 | 29
LTC12000 | 1999-07-16 | 47 | 4 | 0 | 7 | 0 | 179 | 642 | 15889 | 65472 | 11
LTC12000 | 2000-05-11 | 54 | 5 | 0 | 9 | 62 | 227 | 753 | 6803 | 66213 | 14
LTC12000 | 2002-06-26 | 163 | 6 | 2 | 11 | 81 | 209 | 966 | 16040 | 72367 | 19
LTC12000 | 2003-06-26 | 176 | 2 | 1 | 6 | 36 | 259 | 916 | 11025 | 63977 | 9
LTC12000 | 2004-02-25 | 16 | 0 | 0 | 3 | 1 | 40 | 444 | 29283 | 67815 | 3
LTC12000 | 2005-07-25 | 56 | 0 | 0 | 4 | 28 | 293 | 1075 | 11240 | 71155 | 4
LTC12001 | 1993-09-03 | 232 | 0 | 8 | 39 | 151 | 48 | 402 | 35486 | 73831 | 47
LTC12001 | 1994-05-13 | 23 | 0 | 2 | 8 | 31 | 104 | 556 | 25296 | 68971 | 10
LTC12001 | 1996-04-03 | 34 | 0 | 3 | 9 | 44 | 33 | 538 | 34191 | 71183 | 12
LTC12001 | 1997-06-10 | 29 | 1 | 0 | 10 | 34 | 88 | 452 | 30733 | 68240 | 11
LTC12001 | 1998-07-23 | 50 | 8 | 0 | 13 | 60 | 201 | 553 | 22258 | 79150 | 21
LTC12001 | 1999-07-16 | 41 | 3 | 0 | 7 | 0 | 203 | 635 | 15268 | 66146 | 10
LTC12001 | 2000-05-11 | 51 | 5 | 0 | 7 | 58 | 97 | 485 | 20391 | 65888 | 12
LTC12001 | 2002-06-26 | 142 | 5 | 1 | 10 | 52 | 253 | 954 | 9318 | 73210 | 16
LTC12001 | 2003-06-26 | 90 | 0 | 0 | 3 | 30 | 151 | 723 | 19730 | 63883 | 3
LTC12001 | 2004-03-12 | 36 | 0 | 0 | 3 | 20 | 70 | 489 | 24360 | 63982 | 3
LTC12001 | 2004-07-13 | 57 | 0 | 0 | 0 | 0 | 166 | 789 | 20126 | 67305 | 0
Note on B9: <- 10 times lab's minimum detection limit
Calculate TDHG

## Ethylene-Acetylene Results
IEEE Std C57.139-2010 Guide for Dissolved Gas Analysis in Transformer Load Tap Changers Statistics Calculator
| Ethylene | Acetylene | Variable | Formula | Ratio of Gas 1 / Gas 2 | Original Ratio of Gas 1 / Gas 2 | LN Ratio of Gas 1 / Gas 2 | Variable | Formula
| #N/A | 11.25 | Q1 | =QUARTILE(Range,1) | #N/A | 0.15464 | 10 | N | =COUNT(Range LN))
| #N/A | 35 | MEDIAN | =MEDIAN(Range) |  |  | -1.711 | Avg | =AVERAGE(Range LN)
| #N/A | 64.75 | Q3 | =QUARTILE(Range,3) | #N/A | 0.31013 | 0.46926 | StdDev | =STDEV(Range LN)
| #N/A | 53.5 | IQR | =Q3 - Q1 | #N/A | 0.15549 | 0.3919 | C0.95 | =EXP(Avg+1.65*StdDev) CAUTION LIMIT
|  |  | U1 | =Q3 + IQR*1.5 | #N/A | 0.54336 | 0.53922 | C0.99 | =EXP(Avg+2.33*StdDev) WARNING LIMIT
| #N/A | 225.25 | U2 | =Q3 + IQR*3 | #N/A | 0.77659 | 0.46186 | C??? | =EXP(Avg+???*StdDev) USER DEFINED LIMIT
| ^ CAUTION LIMITS ^ | [6 empty] | 2 | User Defined Tolerance Bounds
|  |  | 1. Choose the two gases for analysis |  |  |  | 0.29435 | C0.85 | User Selected LogNormal Percentile
|  |  | 2. Click Run Gas Calculations button |  |  |  | 0.77028 | C0.999 | User Selected LogNormal Percentile
3. Click Run Gas Ratio Calculations button
| C2H4 | C2H2 | 4. (Optional) Enter User Defined Tolerance Bounds or Select Percentiles for Ratio Calculations
| Gas 1 | Gas 2 |  |  | 253
| Ethylene | Acetylene |  |  | Gas 1 / Gas 2 | LN (Gas1 / Gas2)
| 0 | 8 | Total Values |  | 0 | 4
| 4 | 38 |  |  | 0.37931 | -0.9694
| 5 | 19 |  |  | 0.11765 | -2.1401
| 3 | 25 |  |  | 0.125 | -2.0794
| 0 | 17 |  |  | 0.081871 | -2.5026
| 0 | 20
| 0 | 24
| 11 | 29
| 0 | 10
| 2 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 1 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 74 | 40
| 3 | 23
| 6 | 57
| 7 | 19
| 3 | 26
| 1 | 21
| 4 | 25
| 3 | 26
| 5 | 30
| 4 | 32
| 4 | 42
| 3 | 17
| 4 | 18
| 4 | 30
| 4 | 18
| 2 | 42
| 5 | 36
| 4 | 26
| 2 | 14
| 0 | 10
| 1 | 9
| 0 | 9
| 0 | 0
| 1 | 0
| 1 | 7
| 1 | 0
| 0 | 0
| 28 | 238
| 18 | 144
| 14 | 171
| 50 | 447
| 58 | 5.2
| 72 | 604
| 64 | 506
| 26 | 100
| 10 | 102
| 10 | 69
| 18 | 168
| 21 | 60
| 5 | 55
| 6 | 45
| 6 | 38
| 1 | 47
| 6 | 44
| 6 | 36
| 7 | 55
| 13 | 69
| 4 | 24
| 0 | 0
| 1 | 4
| 0 | 6
| 0 | 0
| 18 | 157
| 22 | 145
| 15 | 97
| 19 | 115
| 16 | 131
| 20 | 150
| 18 | 161
| 23 | 107
| 19 | 121
| 21 | 171
| 14 | 87
| 12 | 6
| 23 | 73
| 20 | 128
| 14 | 101
| 0 | 0
| 0 | 16
| 8 | 79
| 1 | 13
| 2 | 0
| 38 | 410
| 10 | 110
| 13 | 143
| 3 | 16
| 0 | 11
| 25 | 142
| 4 | 17
| 2 | 14
| 2 | 9
| 48 | 384
| 93 | 759
| 4 | 60
| 30 | 152
| 12 | 76
| 5 | 31
| 0 | 0
| 2 | 0
| 0 | 0
| 5 | 24
| 15 | 104
| 13 | 82
| 10 | 54
| 5 | 41
| 5 | 8
| 3 | 22
| 8 | 34
| 7 | 26
| 4 | 6
| 10 | 33
| 14 | 38
| 0 | 0
| 9 | 51
| 22 | 178
| 6 | 38
| 16 | 102
| 6 | 43
| 5 | 22
| 0 | 7
| 3 | 14
| 6 | 19
| 4 | 29
| 5 | 20
| 8 | 38
| 174 | 554
| 1 | 0
| 83 | 368
| 245 | 923
| 294 | 1082
| 815 | 2602
| 71 | 390
| 14 | 73
| 7 | 53
| 19 | 152
| 11 | 60
| 16 | 101
| 28 | 144
| 3 | 15
| 4 | 16
| 3 | 43
| 3 | 27
| 4 | 2
| 3 | 21
| 5 | 28
| 8 | 37
| 55 | 34
| 9 | 38
| 10 | 43
| 10 | 43
| 13 | 37
| 7 | 56
| 6 | 31
| 16 | 81
| 13 | 60
| 2 | 11
| 0 | 5
| 3 | 12
| 0 | 18
| 3 | 17
| 7 | 38
| 8 | 39
| 4 | 29
| 11 | 76
| 19 | 158
| 12 | 98
| 18 | 117
| 5 | 44
| 35 | 35
| 0 | 9
| 4 | 26
| 4 | 28
| 2 | 30
| 1 | 1
| 3 | 16
| 2 | 15
| 3731 | 149
| 4434 | 163
| 8343 | 211
| 10526 | 274
| 13424 | 360
| 6 | 36
| 9 | 56
| 10 | 48
| 9 | 30
| 16 | 80
| 10 | 58
| 14 | 62
| 17 | 43
| 8 | 35
| 0 | 0
| 3 | 9
| 17 | 51
| 4 | 12
| 20 | 119
| 15 | 102
| 11 | 50
| 22 | 164
| 11 | 82
| 7 | 50
| 10 | 65
| 8 | 50
| 6 | 68
| 22 | 104
| 10 | 66
| 4 | 22
| 3 | 20
| 9 | 63
| 8 | 36
| 13 | 67
| 11 | 37
| 5 | 30
| 12 | 42
| 27 | 37
| 3969 | 263
| 2 | 9
| 2 | 17
| 0 | 0 |  |  | 0.18889 | -1.6666
| 1 | 0 |  |  | 0.1358 | -1.9966
| 1 | 9 |  |  | 0.25828 | -1.3537
| 2 | 10 |  |  | 0.29412 | -1.2238
| 1 | 6 |  |  | 0.21667 | -1.5294
| 3 | 4 |  |  | 0.19231 | -1.6487
| 8 | 56
| 7 | 53
| 8 | 57
| 23 | 73
| 8 | 64
| 14 | 68
| 5 | 40
| 18 | 44
| 7 | 46
| 18 | 99
| 26 | 146
| 11 | 35
| 19 | 90
| 9 | 46
| 10 | 42
| 0 | 0
| 6 | 34
| 6 | 22
| 5 | 39
| 9 | 49
| 0 | 28
| 5 | 61
| 3 | 21
| 2 | 2
| 2 | 6
| 2 | 4
| 0 | 4
| 10 | 14
| 8 | 12
| 3 | 9
| 2 | 4
| 0 | 0
| 3 | 3
| 1 | 22
| 19 | 120
| 15 | 118
| 8 | 86
| 17 | 98
| 0 | 5
| 5 | 49
| 3 | 13
| 2 | 14
| 1 | 0
| 0 | 0
| 7709 | 222
| 8733 | 301
| 12346 | 426
| 14 | 7
| 0 | 0
| 32 | 45
| 11 | 23
| 17 | 76
| 22 | 93
| 1 | 0
| 6 | 42
| 7 | 9
| 11 | 41
| 4 | 14
| 5 | 31
| 4 | 0
| 6 | 28
| 11833 | 374
| 8504 | 243
| 9 | 73
| 10 | 43
| 10 | 54
| 13 | 61
| 14 | 108
| 10 | 40
| 14 | 68
| 9 | 55
| 7 | 47
| 8 | 23
| 6 | 33
| 9 | 45
| 6 | 36
| 6 | 0
| 137 | 388
| 5 | 5
| 3 | 14
| 17 | 46
| 8 | 35
| 11 | 39
| 8 | 48
| 9 | 40
| 14 | 55
| 17 | 79
| 12 | 43
| 4 | 11
| 4 | 15
| 6 | 25
| 4 | 0
| 4 | 24
| 6 | 25
| 7 | 24
| 308 | 1315
| 14 | 27
| 14 | 77
| 14 | 97
| 19 | 154
| 19 | 186
| 17 | 124
| 16 | 68
| 7 | 37
| 8 | 49
| 14 | 82
| 10 | 59
| 9 | 39
| 8 | 37
| 14 | 55
| 6 | 33
| 31 | 31
| 5 | 34
| 5 | 33
| 6 | 0
| 2 | 15
| 18 | 155
| 1 | 1
| 0 | 2
| 0 | 0
| 0 | 0
| 6 | 41
| 3 | 28
| 0 | 24
| 20 | 17
| 5 | 38
| 2 | 0
| 0 | 10
| 10 | 81
| 1 | 5
| 2 | 3
| 0 | 7
| 0 | 0
| 0 | 0
| 32 | 0
| 36 | 0
| 1 | 0
| 7 | 0
| 70 | 0
| 25 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 4 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 94 | 743
| 187 | 1476
| 362 | 2716
| 104 | 139
| 48 | 333
| 7 | 44
| 15 | 76
| 10 | 67
| 8 | 59
| 21 | 135
| 7 | 48
| 12 | 68
| 14 | 17
| 15 | 75
| 12 | 46
| 33 | 123
| 11 | 252
| 24 | 81
| 27 | 113
| 16 | 72
| 29 | 86
| 3 | 0
| 60 | 153
| 20 | 0
| 308 | 1890
| 279 | 1612
| 31 | 153
| 55 | 148
| 58 | 194
| 76 | 441
| 97 | 448
| 65 | 220
| 40 | 1
| 16 | 53
| 5 | 19
| 5 | 21
| 6 | 8
| 12 | 35
| 12 | 13
| 0 | 0
| 1 | 18
| 13 | 125
| 9 | 66
| 0 | 3
| 2 | 5
| 0 | 8
| 0 | 9
| 11 | 89
| 15 | 57
| 14 | 77
| 8 | 68
| 11 | 30
| 12 | 12
| 0 | 0
| 0 | 0
| 8 | 25
| 1 | 0
| 4 | 19
| 3 | 24
| 5 | 26
| 1 | 0
| 2 | 0
| 0 | 0
| 11 | 45
| 4 | 21
| 7 | 36
| 7 | 23
| 4 | 22
| 0 | 14
| 0 | 0
| 0 | 4
| 0 | 8
| 3 | 13
| 0 | 14
| 0 | 8
| 2 | 12
| 9 | 50
| 8 | 37
| 9 | 53
| 9 | 60
| 3 | 10
| 6 | 47
| 7 | 53
| 8 | 42
| 2 | 22
| 4 | 36
| 10 | 77
| 6 | 36
| 5 | 32
| 8 | 36
| 10 | 13
| 2 | 4
| 3 | 24
| 0 | 18
| 11 | 25
| 2 | 36
| 0 | 1
| 3 | 16
| 0 | 1
| 0 | 0
| 2 | 0
| 2 | 11
| 3 | 11
| 0 | 0
| 3 | 18
| 14 | 41
| 7 | 54
| 8 | 80
| 6 | 46
| 0 | 7
| 4 | 24
| 7 | 13
| 4 | 11
| 2 | 2
| 0 | 0
| 8 | 68
| 6 | 36
| 8 | 43
| 4 | 36
| 4 | 42
| 7 | 27
| 2 | 12
| 3 | 16
| 0 | 0
| 2 | 21
| 4 | 36
| 4 | 38
| 4 | 29
| 5 | 42
| 26 | 36
| 3 | 12
| 0 | 0
| 3 | 0
| 42 | 259
| 25 | 191
| 28 | 202
| 22 | 150
| 6 | 37
| 9 | 41
| 19 | 52
| 7 | 32
| 5 | 22
| 5 | 20
| 16 | 74
| 5 | 29
| 15 | 58
| 10 | 71
| 10 | 62
| 13 | 59
| 6 | 30
| 17 | 68
| 9 | 50
| 7 | 45
| 11 | 49
| 13 | 86
| 8 | 57
| 20 | 75
| 8 | 40
| 6 | 28
| 0 | 3
| 6 | 32
| 4 | 21
| 6 | 32
| 4 | 1
| 69 | 460
| 0 | 0
| 62 | 5
| 42 | 82
| 9 | 43
| 13 | 84
| 19 | 151
| 12 | 95
| 11 | 70
| 8 | 67
| 10 | 52
| 7 | 45
| 6 | 40
| 7 | 29
| 0 | 6
| 0 | 9
| 1 | 0
| 2 | 9
| 6 | 40
| 5 | 35
| 6 | 46
| 4 | 26
| 31 | 29
| 8 | 41
| 0 | 1
| 0 | 0
| 0 | 0
| 0 | 4
| 6 | 0
| 3 | 0
| 13 | 95
| 5 | 30
| 274 | 16
| 20 | 51
| 293 | 72
| 4 | 29
| 6 | 29
| 0 | 5
| 2 | 7
| 2 | 10
| 1 | 1
| 1 | 0
| 2 | 47
| 9 | 6
| 57 | 259
| 58 | 269
| 32 | 151
| 29 | 130
| 25 | 148
| 28 | 129
| 49 | 158
| 49 | 179
| 216 | 553
| 29 | 13
| 41 | 120
| 138 | 793
| 222 | 1328
| 10 | 57
| 4 | 17
| 3 | 11
| 3 | 0
| 0 | 21
| 2 | 14
| 4 | 16
| 8 | 12
| 2 | 2
| 0 | 0
| 0 | 0
| 45 | 2239
| 36 | 181
| 38 | 200
| 28 | 158
| 30 | 271
| 42577 | 630
| 110 | 359
| 44 | 194
| 40 | 161
| 36 | 146
| 7 | 25
| 4 | 45
| 6 | 35
| 8 | 39
| 5 | 27
| 4 | 30
| 0 | 8
| 2 | 6
| 0 | 8
| 3 | 22
| 0 | 8
| 0 | 4
| 11 | 47
| 7 | 45
| 8 | 50
| 7 | 47
| 0 | 26
| 5 | 24
| 0 | 0
| 1 | 8
| 2 | 6
| 0 | 4
| 2 | 8
| 9 | 58
| 8 | 49
| 8 | 48
| 5 | 38
| 29 | 44
| 4 | 37
| 0 | 14
| 3 | 6
| 6 | 5
| 4 | 14
| 6 | 20
| 5 | 22
| 4 | 12
| 12 | 86
| 6 | 32
| 9 | 45
| 5 | 43
| 6 | 73
| 5 | 43
| 0 | 8
| 1 | 21
| 3 | 7
| 2 | 1
| 0 | 0
| 7 | 37
| 2 | 12
| 13 | 39
| 4 | 19
| 2 | 24
| 2 | 12
| 2 | 18
| 5 | 23
| 12 | 52
| 6 | 43
| 18 | 104
| 20 | 51
| 0 | 0
| 3 | 11
| 11 | 56
| 15 | 43
| 6 | 58
| 11 | 56
| 4 | 50
| 13 | 50
| 4 | 34
| 0 | 6
| 4 | 13
| 0 | 0
| 4 | 12
| 3 | 8
| 7 | 7
| 23 | 1
| 14 | 66
| 6 | 45
| 6 | 45
| 3 | 30
| 7 | 49
| 5 | 31
| 5 | 40
| 3 | 20
| 3 | 25
| 13 | 36
| 3 | 28
| 42 | 180
| 12 | 58
| 12 | 63
| 13 | 66
| 17 | 90
| 7 | 0
| 9 | 62
| 11 | 81
| 6 | 36
| 3 | 1
| 4 | 28
| 39 | 151
| 8 | 31
| 9 | 44
| 10 | 34
| 13 | 60
| 7 | 0
| 7 | 58
| 10 | 52
| 3 | 30
| 3 | 20
| 0 | 0
Run Gas Calculations
Run Gas Ratio Calculations

## TDHG-Acetylene Results
IEEE Std C57.139-2010 Guide for Dissolved Gas Analysis in Transformer Load Tap Changers Statistics Calculator
| TDHG | Acetylene | Variable | Formula | Ratio of Gas 1 / Gas 2 | Original Ratio of Gas 1 / Gas 2 | LN Ratio of Gas 1 / Gas 2 | Variable | Formula
| #N/A | 11.25 | Q1 | =QUARTILE(Range,1) | #N/A | 0.21308 | 216 | N | =COUNT(Range LN))
| #N/A | 35 | MEDIAN | =MEDIAN(Range) |  |  | -1.2926 | Avg | =AVERAGE(Range LN)
| #N/A | 64.75 | Q3 | =QUARTILE(Range,3) | #N/A | 0.40628 | 0.4475 | StdDev | =STDEV(Range LN)
| #N/A | 53.5 | IQR | =Q3 - Q1 | #N/A | 0.19321 | 0.57452 | C0.95 | =EXP(Avg+1.65*StdDev) CAUTION LIMIT
|  |  | U1 | =Q3 + IQR*1.5 | #N/A | 0.69609 | 0.77886 | C0.99 | =EXP(Avg+2.33*StdDev) WARNING LIMIT
| #N/A | 225.25 | U2 | =Q3 + IQR*3 | #N/A | 0.9859 | 0.67193 | C??? | =EXP(Avg+???*StdDev) USER DEFINED LIMIT
| ^ CAUTION LIMITS ^ | [6 empty] | 2 | User Defined Tolerance Bounds
|  |  | 1. Choose the two gases for analysis |  |  |  | 0.43727 | C0.85 | User Selected LogNormal Percentile
|  |  | 2. Click Run Gas Calculations button |  |  |  | 1.0944 | C0.999 | User Selected LogNormal Percentile
3. Click Run Gas Ratio Calculations button
| TDHG | C2H2 | 4. (Optional) Enter User Defined Tolerance Bounds or Select Percentiles for Ratio Calculations
| Gas 1 | Gas 2 |  |  | 244
| TDHG | Acetylene |  |  | Gas 1 / Gas 2 | LN (Gas1 / Gas2)
| 0 | 8 | Total Values |  | 0 | 8
| 4 | 38 |  |  | 0.68421 | -0.37949
| 13 | 19 |  |  | 0.11765 | -2.1401
| 5 | 25 |  |  | 0.15972 | -1.8343
| 0 | 17 |  |  | 0.18129 | -1.7077
| 2 | 20 |  |  | 0.1745 | -1.7458
| 0 | 24 |  |  | 0.16887 | -1.7786
| 11 | 29 |  |  | 0.16601 | -1.7957
| 0 | 10 |  |  | 0.31 | -1.1712
| 7 | 0 |  |  | 0.21739 | -1.5261
| 2 | 0 |  |  | 0.17857 | -1.7228
| 0 | 0 |  |  | 0.43333 | -0.83625
| 0 | 0 |  |  | 0.27536 | -1.2897
| 2 | 0 |  |  | 0.11465 | -2.1659
| 0 | 0 |  |  | 0.17241 | -1.7579
| 0 | 0 |  |  | 0.15464 | -1.8667
| 0 | 0 |  |  | 0.22609 | -1.4868
| 89 | 40 |  |  | 0.16794 | -1.7842
| 3 | 23 |  |  | 0.19333 | -1.6433
| 6 | 57 |  |  | 0.15528 | -1.8625
| 7 | 19 |  |  | 0.31776 | -1.1465
| 4 | 26 |  |  | 0.19835 | -1.6177
| 1 | 21 |  |  | 0.15789 | -1.8458
| 5 | 25 |  |  | 0.2069 | -1.5755
| 3 | 26 |  |  | 0.31507 | -1.155
| 5 | 30 |  |  | 0.20312 | -1.5939
| 4 | 32 |  |  | 0.16832 | -1.7819
| 4 | 42 |  |  | 0.10732 | -2.232
| 3 | 17 |  |  | 0.13636 | -1.9924
| 4 | 18 |  |  | 0.11888 | -2.1296
| 6 | 30 |  |  | 0.26056 | -1.3449
| 4 | 18 |  |  | 0.15152 | -1.8871
| 3 | 42 |  |  | 0.36184 | -1.0165
| 5 | 36 |  |  | 0.19737 | -1.6227
| 4 | 26 |  |  | 0.41935 | -0.86904
| 2 | 14 |  |  | 0.17308 | -1.754
| 0 | 10 |  |  | 0.18293 | -1.6987
| 1 | 9 |  |  | 0.27778 | -1.2809
| 0 | 9 |  |  | 0.42424 | -0.85745
| 5 | 0 |  |  | 0.65789 | -0.41871
| 7 | 0 |  |  | 0.27528 | -1.29
| 1 | 7 |  |  | 0.2451 | -1.4061
| 1 | 0 |  |  | 0.3917 | -0.93727
| 0 | 0 |  |  | 0.33424 | -1.0959
| 28 | 238 |  |  | 0.34778 | -1.0562
| 23 | 144 |  |  | 0.3586 | -1.0256
| 31 | 171 |  |  | 0.40892 | -0.89424
| 78 | 447 |  |  | 0.28205 | -1.2657
| 85 | 5.2 |  |  | 0.19178 | -1.6514
| 102 | 604 |  |  | 0.21711 | -1.5274
| 84 | 506 |  |  | 0.25 | -1.3863
| 31 | 100 |  |  | 0.21782 | -1.5241
| 10 | 102 |  |  | 0.39583 | -0.92676
| 15 | 69 |  |  | 0.40541 | -0.90287
| 30 | 168 |  |  | 0.37209 | -0.98861
| 26 | 60 |  |  | 0.35135 | -1.046
| 8 | 55 |  |  | 0.25926 | -1.3499
| 8 | 45 |  |  | 0.35 | -1.0498
| 6 | 38 |  |  | 0.21053 | -1.5581
| 1 | 47 |  |  | 0.17089 | -1.7668
| 8 | 44 |  |  | 0.18367 | -1.6946
| 6 | 36 |  |  | 0.20513 | -1.5841
| 7 | 55 |  |  | 0.53333 | -0.62861
| 19 | 69 |  |  | 0.2625 | -1.3375
| 6 | 24 |  |  | 0.22414 | -1.4955
| 0 | 0 |  |  | 0.27419 | -1.2939
| 1 | 4 |  |  | 0.48837 | -0.71668
| 1 | 6 |  |  | 0.37255 | -0.98739
| 1 | 0 |  |  | 0.2521 | -1.3779
| 18 | 157 |  |  | 0.23529 | -1.4469
| 25 | 145 |  |  | 0.66 | -0.41552
| 15 | 97 |  |  | 0.21951 | -1.5163
| 26 | 115 |  |  | 0.18293 | -1.6987
| 22 | 131 |  |  | 0.23077 | -1.4663
| 29 | 150 |  |  | 0.33654 | -1.089
| 25 | 161 |  |  | 0.21212 | -1.5506
| 34 | 107 |  |  | 0.26866 | -1.3143
| 24 | 121 |  |  | 0.38095 | -0.96508
| 27 | 171 |  |  | 0.31507 | -1.155
| 18 | 87 |  |  | 0.26471 | -1.3291
| 17 | 6 |  |  | 0.59091 | -0.52609
| 23 | 73 |  |  | 0.32323 | -1.1294
| 26 | 128 |  |  | 0.26712 | -1.32
| 17 | 101 |  |  | 0.37143 | -0.9904
| 0 | 0 |  |  | 0.28889 | -1.2417
| 0 | 16 |  |  | 0.32609 | -1.1206
| 8 | 79 |  |  | 0.33333 | -1.0986
| 3 | 13 |  |  | 0.26531 | -1.3269
| 5 | 0 |  |  | 0.21667 | -1.5294
| 44 | 410 |  |  | 0.20339 | -1.5926
| 15 | 110 |  |  | 0.21429 | -1.5404
| 17 | 143 |  |  | 0.86667 | -0.1431
| 4 | 16 |  |  | 0.22368 | -1.4975
| 0 | 11 |  |  | 0.30108 | -1.2004
| 37 | 142 |  |  | 0.31707 | -1.1486
| 8 | 17 |  |  | 0.51163 | -0.67016
| 2 | 14 |  |  | 0.21311 | -1.5459
| 2 | 9 |  |  | 0.21296 | -1.5466
| 582 | 384 |  |  | 0.26471 | -1.3291
| 115 | 759 |  |  | 0.5232 | -0.6478
| 4 | 60 |  |  | 0.36957 | -0.99543
| 55 | 152 |  |  | 0.30909 | -1.1741
| 15 | 76 |  |  | 0.21519 | -1.5362
| 13 | 31 |  |  | 0.37643 | -0.97703
| 0 | 0 |  |  | 0.74074 | -0.3001
| 2 | 0 |  |  | 0.18182 | -1.7047
| 0 | 0 |  |  | 0.14433 | -1.9357
| 9 | 24 |  |  | 0.12338 | -2.0925
| 18 | 104 |  |  | 0.10215 | -2.2813
| 15 | 82 |  |  | 0.1371 | -1.9871
| 15 | 54 |  |  | 0.27941 | -1.2751
| 9 | 41 |  |  | 0.28049 | -1.2712
| 5 | 8 |  |  | 0.27119 | -1.3049
| 3 | 22 |  |  | 0.33333 | -1.0986
| 8 | 34 |  |  | 0.40541 | -0.90287
| 9 | 26 |  |  | 0.34545 | -1.0629
| 4 | 6 |  |  | 0.16774 | -1.7853
| 14 | 33 |  |  | 0.18519 | -1.6864
| 25 | 38 |  |  | 0.18708 | -1.6762
| 0 | 0 |  |  | 0.24593 | -1.4027
| 9 | 51 |  |  | 0.26988 | -1.3098
| 49 | 178 |  |  | 0.92806 | -0.074662
| 9 | 38 |  |  | 0.16216 | -1.8192
| 25 | 102 |  |  | 0.19737 | -1.6227
| 6 | 43 |  |  | 0.22963 | -1.4713
| 8 | 22 |  |  | 0.29167 | -1.2321
| 0 | 7 |  |  | 0.19118 | -1.6546
| 5 | 14 |  |  | 0.24 | -1.4271
| 6 | 19 |  |  | 0.35772 | -1.028
| 4 | 29 |  |  | 0.35802 | -1.0272
| 5 | 20 |  |  | 0.29204 | -1.2309
| 8 | 38 |  |  | 0.29167 | -1.2321
| 217 | 554 |  |  | 0.37209 | -0.98861
| 15 | 0 |  |  | 0.43137 | -0.84078
| 123 | 368 |  |  | 0.1873 | -1.675
| 321 | 923 |  |  | 0.20037 | -1.6076
| 388 | 1082 |  |  | 0.22222 | -1.5041
| 1064 | 2602 |  |  | 0.56757 | -0.5664
| 110 | 390 |  |  | 0.37629 | -0.9774
| 14 | 73 |  |  | 0.2381 | -1.4351
| 7 | 53 |  |  | 0.41295 | -0.88444
| 33 | 152 |  |  | 0.7 | -0.35667
| 15 | 60 |  |  | 0.35849 | -1.0259
| 22 | 101 |  |  | 0.4 | -0.91629
| 57 | 144 |  |  | 0.208 | -1.5702
| 6 | 15 |  |  | 0.36842 | -0.99853
| 4 | 16 |  |  | 0.24675 | -1.3994
| 5 | 43 |  |  | 0.56667 | -0.56798
| 3 | 27 |  |  | 0.52 | -0.65393
| 5 | 2 |  |  | 0.28889 | -1.2417
| 4 | 21 |  |  | 0.33333 | -1.0986
| 5 | 28 |  |  | 0.19481 | -1.6358
| 15 | 37 |  |  | 0.56 | -0.57982
| 67 | 34 |  |  | 0.36585 | -1.0055
| 9 | 38 |  |  | 0.2125 | -1.5488
| 10 | 43 |  |  | 0.33591 | -1.0909
| 16 | 43 |  |  | 0.20419 | -1.5887
| 13 | 37 |  |  | 0.28713 | -1.2478
| 10 | 56 |  |  | 0.26 | -1.3471
| 8 | 31 |  |  | 0.42308 | -0.8602
| 21 | 81 |  |  | 0.27027 | -1.3083
| 21 | 60 |  |  | 0.34483 | -1.0647
| 2 | 11 |  |  | 0.27119 | -1.3049
| 0 | 5 |  |  | 0.36765 | -1.0006
| 3 | 12 |  |  | 0.34 | -1.0788
| 1 | 18 |  |  | 0.38776 | -0.94738
| 6 | 17 |  |  | 0.15116 | -1.8894
| 7 | 38 |  |  | 0.26667 | -1.3218
| 8 | 39 |  |  | 0.20435 | -1.5879
| 4 | 29 |  |  | 0.59756 | -0.5149
| 16 | 76 |  |  | 0.15476 | -1.8659
| 27 | 158 |  |  | 0.22517 | -1.4909
| 18 | 98 |  |  | 0.21053 | -1.5581
| 24 | 117 |  |  | 0.32692 | -1.118
| 9 | 44 |  |  | 0.13684 | -1.9889
| 38 | 35 |  |  | 0.45098 | -0.79633
| 1 | 9 |  |  | 0.55172 | -0.59471
| 4 | 26 |  |  | 0.24324 | -1.4137
| 8 | 28 |  |  | 0.2342 | -1.4516
| 2 | 30 |  |  | 0.21192 | -1.5515
| 1 | 1 |  |  | 0.28462 | -1.2566
| 3 | 16 |  |  | 0.19595 | -1.6299
| 4 | 15 |  |  | 0.49612 | -0.70093
| 6069 | 149 |  |  | 0.40506 | -0.90371
| 7048 | 163 |  |  | 0.35754 | -1.0285
| 13567 | 211 |  |  | 0.53165 | -0.63178
| 16711 | 274 |  |  | 0.44167 | -0.8172
| 21037 | 360 |  |  | 0.23581 | -1.4447
| 6 | 36 |  |  | 0.22063 | -1.5113
| 9 | 56 |  |  | 0.023225 | -3.7625
| 10 | 48 |  |  | 0.27072 | -1.3067
| 16 | 30 |  |  | 0.275 | -1.291
| 21 | 80 |  |  | 0.33544 | -1.0923
| 13 | 58 |  |  | 0.15498 | -1.8644
| 17 | 62 |  |  | 0.42618 | -0.85288
| 21 | 43 |  |  | 0.31959 | -1.1407
| 11 | 35 |  |  | 0.32298 | -1.1302
| 0 | 0 |  |  | 0.32192 | -1.1335
| 3 | 9 |  |  | 0.84091 | -0.17327
| 19 | 51 |  |  | 0.38462 | -0.95551
| 6 | 12 |  |  | 0.34615 | -1.0609
| 30 | 119 |  |  | 0.22115 | -1.5089
| 24 | 102 |  |  | 0.54902 | -0.59962
| 33 | 50 |  |  | 0.34884 | -1.0531
| 36 | 164 |  |  | 0.25 | -1.3863
| 15 | 82 |  |  | 0.26 | -1.3471
| 12 | 50 |  |  | 0.21212 | -1.5506
| 15 | 65 |  |  | 0.26531 | -1.3269
| 11 | 50 |  |  | 0.5 | -0.69315
| 11 | 68 |  |  | 0.24444 | -1.4088
| 35 | 104 |  |  | 0.25758 | -1.3564
| 14 | 66 |  |  | 0.32222 | -1.1325
| 7 | 22 |  |  | 0.22581 | -1.4881
| 5 | 20 |  |  | 0.23457 | -1.45
| 9 | 63 |  |  | 0.31126 | -1.1671
| 8 | 36 |  |  | 0.35 | -1.0498
| 18 | 67 |  |  | 0.30769 | -1.1787
| 11 | 37
| 5 | 30
| 16 | 42
| 77 | 37
| 5843 | 263
| 2 | 9
| 2 | 17
| 0 | 0
| 5 | 0
| 1 | 9
| 2 | 10
| 1 | 6
| 3 | 4
| 8 | 56
| 7 | 53
| 8 | 57
| 23 | 73
| 8 | 64
| 18 | 68
| 7 | 40
| 26 | 44
| 12 | 46
| 32 | 99
| 39 | 146
| 13 | 35
| 26 | 90
| 15 | 46
| 14 | 42
| 0 | 0
| 8 | 34
| 9 | 22
| 5 | 39
| 13 | 49
| 0 | 28
| 9 | 61
| 3 | 21
| 3 | 2
| 2 | 6
| 2 | 4
| 4 | 4
| 10 | 14
| 8 | 12
| 3 | 9
| 2 | 4
| 3 | 0
| 3 | 3
| 1 | 22
| 26 | 120
| 24 | 118
| 12 | 86
| 21 | 98
| 0 | 5
| 7 | 49
| 10 | 13
| 2 | 14
| 1 | 0
| 3 | 0
| 11717 | 222
| 12920 | 301
| 18908 | 426
| 23 | 7
| 0 | 0
| 39 | 45
| 11 | 23
| 17 | 76
| 28 | 93
| 2 | 0
| 6 | 42
| 8 | 9
| 13 | 41
| 4 | 14
| 5 | 31
| 7 | 0
| 6 | 28
| 19185 | 374
| 14553 | 243
| 10 | 73
| 22 | 43
| 12 | 54
| 13 | 61
| 23 | 108
| 10 | 40
| 18 | 68
| 11 | 55
| 10 | 47
| 11 | 23
| 6 | 33
| 9 | 45
| 10 | 36
| 12 | 0
| 203 | 388
| 8 | 5
| 5 | 14
| 17 | 46
| 8 | 35
| 11 | 39
| 10 | 48
| 9 | 40
| 17 | 55
| 17 | 79
| 12 | 43
| 5 | 11
| 4 | 15
| 7 | 25
| 14 | 0
| 4 | 24
| 10 | 25
| 11 | 24
| 495 | 1315
| 20 | 27
| 14 | 77
| 14 | 97
| 19 | 154
| 19 | 186
| 17 | 124
| 19 | 68
| 8 | 37
| 8 | 49
| 23 | 82
| 16 | 59
| 13 | 39
| 15 | 37
| 19 | 55
| 9 | 33
| 39 | 31
| 8 | 34
| 9 | 33
| 27 | 0
| 2 | 15
| 26 | 155
| 1 | 1
| 0 | 2
| 0 | 0
| 0 | 0
| 6 | 41
| 6 | 28
| 0 | 24
| 49 | 17
| 5 | 38
| 22 | 0
| 0 | 10
| 15 | 81
| 1 | 5
| 2 | 3
| 3 | 7
| 0 | 0
| 0 | 0
| 38 | 0
| 39 | 0
| 2 | 0
| 7 | 0
| 125 | 0
| 44 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 5 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 139 | 743
| 363 | 1476
| 733 | 2716
| 129 | 139
| 54 | 333
| 7 | 44
| 15 | 76
| 10 | 67
| 8 | 59
| 31 | 135
| 14 | 48
| 13 | 68
| 18 | 17
| 18 | 75
| 12 | 46
| 44 | 123
| 11 | 252
| 29 | 81
| 33 | 113
| 21 | 72
| 32 | 86
| 3 | 0
| 66 | 153
| 20 | 0
| 354 | 1890
| 323 | 1612
| 34 | 153
| 84 | 148
| 73 | 194
| 105 | 441
| 185 | 448
| 154 | 220
| 48 | 1
| 19 | 53
| 5 | 19
| 5 | 21
| 10 | 8
| 14 | 35
| 12 | 13
| 1 | 0
| 2 | 18
| 26 | 125
| 12 | 66
| 0 | 3
| 2 | 5
| 0 | 8
| 0 | 9
| 11 | 89
| 21 | 57
| 19 | 77
| 8 | 68
| 17 | 30
| 17 | 12
| 0 | 0
| 0 | 0
| 13 | 25
| 1 | 0
| 4 | 19
| 3 | 24
| 11 | 26
| 3 | 0
| 5 | 0
| 0 | 0
| 13 | 45
| 4 | 21
| 7 | 36
| 7 | 23
| 7 | 22
| 0 | 14
| 0 | 0
| 0 | 4
| 0 | 8
| 3 | 13
| 0 | 14
| 0 | 8
| 2 | 12
| 12 | 50
| 8 | 37
| 9 | 53
| 12 | 60
| 3 | 10
| 9 | 47
| 11 | 53
| 14 | 42
| 2 | 22
| 10 | 36
| 15 | 77
| 9 | 36
| 9 | 32
| 8 | 36
| 10 | 13
| 2 | 4
| 3 | 24
| 0 | 18
| 14 | 25
| 3 | 36
| 0 | 1
| 3 | 16
| 0 | 1
| 0 | 0
| 2 | 0
| 2 | 11
| 3 | 11
| 0 | 0
| 3 | 18
| 15 | 41
| 7 | 54
| 17 | 80
| 6 | 46
| 4 | 7
| 6 | 24
| 7 | 13
| 5 | 11
| 3 | 2
| 0 | 0
| 8 | 68
| 6 | 36
| 11 | 43
| 4 | 36
| 4 | 42
| 8 | 27
| 6 | 12
| 3 | 16
| 0 | 0
| 4 | 21
| 4 | 36
| 8 | 38
| 36 | 29
| 5 | 42
| 36 | 36
| 3 | 12
| 0 | 0
| 10 | 0
| 87 | 259
| 39 | 191
| 58 | 202
| 39 | 150
| 8 | 37
| 11 | 41
| 22 | 52
| 7 | 32
| 5 | 22
| 6 | 20
| 20 | 74
| 5 | 29
| 20 | 58
| 10 | 71
| 10 | 62
| 16 | 59
| 7 | 30
| 25 | 68
| 17 | 50
| 11 | 45
| 19 | 49
| 13 | 86
| 8 | 57
| 20 | 75
| 9 | 40
| 9 | 28
| 0 | 3
| 6 | 32
| 6 | 21
| 8 | 32
| 5 | 1
| 94 | 460
| 2 | 0
| 90 | 5
| 49 | 82
| 11 | 43
| 13 | 84
| 34 | 151
| 20 | 95
| 11 | 70
| 8 | 67
| 17 | 52
| 10 | 45
| 9 | 40
| 9 | 29
| 0 | 6
| 0 | 9
| 4 | 0
| 2 | 9
| 9 | 40
| 5 | 35
| 6 | 46
| 7 | 26
| 38 | 29
| 12 | 41
| 1 | 1
| 0 | 0
| 0 | 0
| 0 | 4
| 8 | 0
| 3 | 0
| 13 | 95
| 5 | 30
| 607 | 16
| 23 | 51
| 459 | 72
| 16 | 29
| 9 | 29
| 0 | 5
| 3 | 7
| 2 | 10
| 1 | 1
| 1 | 0
| 3 | 47
| 9 | 6
| 63 | 259
| 63 | 269
| 32 | 151
| 37 | 130
| 29 | 148
| 64 | 129
| 64 | 158
| 64 | 179
| 294 | 553
| 36 | 13
| 53 | 120
| 187 | 793
| 293 | 1328
| 10 | 57
| 4 | 17
| 3 | 11
| 5 | 0
| 3 | 21
| 4 | 14
| 4 | 16
| 14 | 12
| 6 | 2
| 3 | 0
| 0 | 0
| 52 | 2239
| 49 | 181
| 55 | 200
| 53 | 158
| 42 | 271
| 72199 | 630
| 153 | 359
| 62 | 194
| 52 | 161
| 47 | 146
| 7 | 25
| 4 | 45
| 6 | 35
| 8 | 39
| 5 | 27
| 6 | 30
| 0 | 8
| 2 | 6
| 2 | 8
| 3 | 22
| 0 | 8
| 0 | 4
| 12 | 47
| 7 | 45
| 10 | 50
| 7 | 47
| 0 | 26
| 5 | 24
| 0 | 0
| 1 | 8
| 2 | 6
| 0 | 4
| 2 | 8
| 9 | 58
| 8 | 49
| 10 | 48
| 6 | 38
| 37 | 44
| 4 | 37
| 0 | 14
| 3 | 6
| 12 | 5
| 4 | 14
| 7 | 20
| 6 | 22
| 4 | 12
| 12 | 86
| 6 | 32
| 10 | 45
| 5 | 43
| 8 | 73
| 7 | 43
| 0 | 8
| 1 | 21
| 3 | 7
| 2 | 1
| 0 | 0
| 7 | 37
| 3 | 12
| 15 | 39
| 6 | 19
| 2 | 24
| 6 | 12
| 2 | 18
| 8 | 23
| 18 | 52
| 6 | 43
| 23 | 104
| 28 | 51
| 0 | 0
| 3 | 11
| 11 | 56
| 15 | 43
| 8 | 58
| 14 | 56
| 6 | 50
| 13 | 50
| 11 | 34
| 0 | 6
| 5 | 13
| 0 | 0
| 4 | 12
| 3 | 8
| 12 | 7
| 28 | 1
| 14 | 66
| 6 | 45
| 9 | 45
| 6 | 30
| 13 | 49
| 8 | 31
| 7 | 40
| 5 | 20
| 3 | 25
| 18 | 36
| 5 | 28
| 44 | 180
| 12 | 58
| 12 | 63
| 17 | 66
| 29 | 90
| 11 | 0
| 14 | 62
| 19 | 81
| 9 | 36
| 3 | 1
| 4 | 28
| 47 | 151
| 10 | 31
| 12 | 44
| 11 | 34
| 21 | 60
| 10 | 0
| 12 | 58
| 16 | 52
| 3 | 30
| 3 | 20
| 0 | 0
Run Gas Calculations
Run Gas Ratio Calculations

## Ethane-Methane Results
IEEE Std C57.139-2010 Guide for Dissolved Gas Analysis in Transformer Load Tap Changers Statistics Calculator
| Ethane | Methane | Variable | Formula | Ratio of Gas 1 / Gas 2 | Original Ratio of Gas 1 / Gas 2 | LN Ratio of Gas 1 / Gas 2 | Variable | Formula
| 0 | 0 | Q1 | =QUARTILE(Range,1) | #N/A | 0.29034 | 34 | N | =COUNT(Range LN))
| 0 | 0 | MEDIAN | =MEDIAN(Range) |  |  | -1.032 | Avg | =AVERAGE(Range LN)
| 2 | 4 | Q3 | =QUARTILE(Range,3) | #N/A | 0.57707 | 0.66714 | StdDev | =STDEV(Range LN)
| 2 | 4 | IQR | =Q3 - Q1 | #N/A | 0.28672 | 1.0711 | C0.95 | =EXP(Avg+1.65*StdDev) CAUTION LIMIT
|  |  | U1 | =Q3 + IQR*1.5 | #N/A | 1.0072 | 1.686 | C0.99 | =EXP(Avg+2.33*StdDev) WARNING LIMIT
| 8 | 16 | U2 | =Q3 + IQR*3 | #N/A | 1.4372 | 1.3529 | C??? | =EXP(Avg+???*StdDev) USER DEFINED LIMIT
| ^ CAUTION LIMITS ^ | [6 empty] | 2 | User Defined Tolerance Bounds
|  |  | 1. Choose the two gases for analysis |  |  |  | 0.71303 | C0.85 | User Selected LogNormal Percentile
|  |  | 2. Click Run Gas Calculations button |  |  |  | 2.7994 | C0.999 | User Selected LogNormal Percentile
3. Click Run Gas Ratio Calculations button
| C2H6 | CH4 | 4. (Optional) Enter User Defined Tolerance Bounds or Select Percentiles for Ratio Calculations
| Gas 1 | Gas 2 |  |  | 38
| Ethane | Methane |  |  | Gas 1 / Gas 2 | LN (Gas1 / Gas2)
| 726 | 8 | Total Values |  | 0 | 8
| 0 | 0 |  |  | 0.53571 | -0.62415
| 7 | 1 |  |  | 0.2459 | -1.4028
| 0 | 2 |  |  | 0.27027 | -1.3083
| 0 | 0 |  |  | 0.29688 | -1.2144
| 0 | 2 |  |  | 1.2308 | 0.20764
| 0 | 0 |  |  | 0.2755 | -1.2892
| 0 | 0 |  |  | 0.29023 | -1.2371
| 0 | 0 |  |  | 0.37401 | -0.98346
| 5 | 0 |  |  | 0.3902 | -0.9411
| 0 | 2 |  |  | 0.39945 | -0.91767
| 0 | 0 |  |  | 1.2 | 0.18232
| 0 | 0 |  |  | 0.37189 | -0.98916
| 1 | 0 |  |  | 0.4345 | -0.83355
| 0 | 0 |  |  | 0.41836 | -0.87141
| 0 | 0 |  |  | 0.45177 | -0.79458
| 0 | 0 |  |  | 0.34899 | -1.0527
| 15 | 0 |  |  | 0.35203 | -1.044
| 0 | 0 |  |  | 0.17857 | -1.7228
| 0 | 0 |  |  | 0.12651 | -2.0675
| 0 | 0 |  |  | 0.22222 | -1.5041
| 0 | 1 |  |  | 0.08642 | -2.4485
| 0 | 0 |  |  | 0.050992 | -2.9761
| 0 | 1 |  |  | 0.31429 | -1.1575
| 0 | 0 |  |  | 0.57143 | -0.55962
| 0 | 0 |  |  | 1.2308 | 0.20764
| 0 | 0 |  |  | 0.45455 | -0.78846
| 0 | 0 |  |  | 0.36364 | -1.0116
| 0 | 0 |  |  | 0.57895 | -0.54654
| 0 | 0 |  |  | 0.2907 | -1.2355
| 0 | 2 |  |  | 0.31746 | -1.1474
| 0 | 0 |  |  | 0.5 | -0.69315
| 0 | 1 |  |  | 0.20339 | -1.5926
| 0 | 0 |  |  | 0.73533 | -0.30744
| 0 | 0 |  |  | 0.65385 | -0.42488
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 5 | 0
| 4 | 2
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 5
| 0 | 17
| 0 | 28
| 4 | 23
| 5 | 25
| 2 | 18
| 1 | 4
| 0 | 0
| 5 | 0
| 2 | 10
| 0 | 5
| 0 | 3
| 0 | 2
| 0 | 0
| 0 | 0
| 0 | 2
| 0 | 0
| 0 | 0
| 0 | 6
| 0 | 2
| 0 | 0
| 0 | 0
| 1 | 0
| 0 | 1
| 0 | 0
| 3 | 0
| 0 | 0
| 3 | 4
| 0 | 6
| 0 | 9
| 0 | 7
| 0 | 11
| 0 | 5
| 0 | 6
| 0 | 4
| 0 | 5
| 0 | 0
| 0 | 6
| 0 | 3
| 0 | 0
| 0 | 0
| 0 | 0
| 2 | 0
| 0 | 3
| 6 | 0
| 0 | 5
| 0 | 4
| 1 | 0
| 0 | 0
| 0 | 12
| 2 | 2
| 0 | 0
| 0 | 0
| 3 | 531
| 5 | 17
| 0 | 0
| 5 | 20
| 0 | 3
| 6 | 2
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 4
| 3 | 0
| 2 | 0
| 5 | 0
| 4 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 2 | 0
| 0 | 0
| 4 | 0
| 3 | 8
| 0 | 0
| 0 | 0
| 7 | 20
| 2 | 1
| 3 | 6
| 0 | 0
| 0 | 3
| 0 | 0
| 0 | 2
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 15 | 28
| 0 | 14
| 4 | 36
| 15 | 61
| 20 | 74
| 57 | 192
| 5 | 34
| 0 | 0
| 0 | 0
| 0 | 14
| 0 | 4
| 2 | 4
| 16 | 13
| 1 | 2
| 0 | 0
| 0 | 2
| 0 | 0
| 0 | 1
| 1 | 0
| 0 | 0
| 0 | 7
| 12 | 0
| 0 | 0
| 0 | 0
| 6 | 0
| 0 | 0
| 0 | 3
| 0 | 2
| 1 | 4
| 1 | 7
| 0 | 0
| 0 | 0
| 0 | 0
| 1 | 0
| 0 | 3
| 0 | 0
| 0 | 0
| 0 | 0
| 2 | 3
| 0 | 8
| 0 | 6
| 0 | 6
| 0 | 4
| 0 | 3
| 1 | 0
| 0 | 0
| 4 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 2
| 505 | 1833
| 588 | 2026
| 1422 | 3802
| 1736 | 4449
| 2173 | 5440
| 0 | 0
| 0 | 0
| 0 | 0
| 7 | 0
| 0 | 5
| 1 | 2
| 0 | 3
| 0 | 4
| 0 | 3
| 0 | 0
| 0 | 0
| 2 | 0
| 0 | 2
| 10 | 0
| 9 | 0
| 12 | 10
| 2 | 12
| 0 | 4
| 0 | 5
| 0 | 5
| 0 | 3
| 0 | 5
| 0 | 13
| 0 | 4
| 0 | 3
| 0 | 2
| 0 | 0
| 0 | 0
| 0 | 5
| 0 | 0
| 0 | 0
| 0 | 4
| 3 | 47
| 508 | 1366
| 0 | 0
| 0 | 0
| 0 | 0
| 4 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 4
| 0 | 2
| 3 | 5
| 2 | 3
| 4 | 10
| 0 | 13
| 0 | 2
| 1 | 6
| 0 | 6
| 0 | 4
| 0 | 0
| 2 | 0
| 3 | 0
| 0 | 0
| 0 | 4
| 0 | 0
| 0 | 4
| 0 | 0
| 1 | 0
| 0 | 0
| 0 | 0
| 0 | 4
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 3
| 0 | 0
| 0 | 0
| 7 | 0
| 1 | 8
| 0 | 4
| 0 | 4
| 0 | 0
| 0 | 2
| 0 | 7
| 0 | 0
| 0 | 0
| 3 | 0
| 1214 | 2794
| 1235 | 2952
| 2042 | 4520
| 9 | 0
| 0 | 0
| 7 | 0
| 0 | 0
| 0 | 0
| 0 | 6
| 1 | 0
| 0 | 0
| 0 | 1
| 0 | 2
| 0 | 0
| 0 | 0
| 3 | 0
| 0 | 0
| 1902 | 5450
| 1575 | 4474
| 1 | 0
| 12 | 0
| 2 | 0
| 0 | 0
| 0 | 9
| 0 | 0
| 0 | 4
| 2 | 0
| 0 | 3
| 0 | 3
| 0 | 0
| 0 | 0
| 0 | 4
| 0 | 6
| 10 | 56
| 0 | 3
| 0 | 2
| 0 | 0
| 0 | 0
| 0 | 0
| 2 | 0
| 0 | 0
| 0 | 3
| 0 | 0
| 0 | 0
| 0 | 1
| 0 | 0
| 0 | 1
| 7 | 3
| 0 | 0
| 0 | 4
| 0 | 4
| 21 | 166
| 1 | 5
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 3
| 0 | 1
| 0 | 0
| 0 | 9
| 0 | 6
| 0 | 4
| 2 | 5
| 0 | 5
| 3 | 0
| 8 | 0
| 3 | 0
| 0 | 4
| 5 | 16
| 0 | 0
| 0 | 8
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 3 | 0
| 0 | 0
| 3 | 26
| 0 | 0
| 7 | 13
| 0 | 0
| 0 | 5
| 0 | 0
| 0 | 0
| 3 | 0
| 0 | 0
| 0 | 0
| 6 | 0
| 3 | 0
| 1 | 0
| 0 | 0
| 10 | 45
| 5 | 14
| 0 | 0
| 0 | 0
| 0 | 0
| 1 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 3 | 42
| 14 | 162
| 18 | 353
| 25 | 0
| 6 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 10
| 4 | 3
| 1 | 0
| 0 | 4
| 0 | 3
| 0 | 0
| 1 | 10
| 0 | 0
| 1 | 4
| 0 | 6
| 2 | 3
| 0 | 3
| 0 | 0
| 6 | 0
| 0 | 0
| 11 | 35
| 16 | 28
| 3 | 0
| 16 | 13
| 3 | 12
| 5 | 24
| 73 | 15
| 78 | 11
| 4 | 4
| 3 | 0
| 0 | 0
| 0 | 0
| 2 | 2
| 0 | 2
| 0 | 0
| 1 | 0
| 1 | 0
| 6 | 7
| 0 | 3
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 6 | 0
| 0 | 5
| 0 | 0
| 2 | 4
| 3 | 2
| 0 | 0
| 0 | 0
| 0 | 5
| 0 | 0
| 0 | 0
| 0 | 0
| 6 | 0
| 2 | 0
| 3 | 0
| 0 | 0
| 0 | 2
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 3
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 3 | 0
| 0 | 0
| 0 | 0
| 3 | 0
| 0 | 0
| 0 | 3
| 2 | 2
| 1 | 5
| 0 | 0
| 0 | 6
| 0 | 5
| 0 | 3
| 0 | 4
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 3
| 1 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 1 | 0
| 0 | 0
| 0 | 9
| 0 | 0
| 3 | 1
| 0 | 2
| 0 | 0
| 1 | 0
| 1 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 3 | 0
| 0 | 0
| 0 | 0
| 0 | 1
| 4 | 0
| 0 | 0
| 0 | 0
| 0 | 2
| 0 | 0
| 2 | 2
| 10 | 22
| 0 | 0
| 6 | 4
| 0 | 0
| 0 | 0
| 7 | 0
| 12 | 33
| 0 | 14
| 11 | 19
| 3 | 14
| 0 | 2
| 0 | 2
| 0 | 3
| 0 | 0
| 0 | 0
| 1 | 0
| 4 | 0
| 0 | 0
| 5 | 0
| 0 | 0
| 0 | 0
| 0 | 3
| 0 | 1
| 3 | 5
| 1 | 7
| 0 | 4
| 2 | 6
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 1
| 0 | 3
| 0 | 0
| 0 | 0
| 0 | 2
| 0 | 2
| 0 | 1
| 4 | 21
| 0 | 2
| 18 | 10
| 7 | 0
| 2 | 0
| 0 | 0
| 15 | 0
| 0 | 8
| 0 | 0
| 0 | 0
| 2 | 5
| 0 | 3
| 0 | 3
| 0 | 2
| 0 | 0
| 0 | 0
| 1 | 2
| 0 | 0
| 3 | 0
| 0 | 0
| 0 | 0
| 3 | 0
| 3 | 4
| 0 | 4
| 1 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 2 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 75 | 258
| 3 | 0
| 40 | 126
| 7 | 5
| 0 | 3
| 0 | 0
| 0 | 1
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 1
| 0 | 0
| 6 | 0
| 5 | 0
| 0 | 0
| 2 | 6
| 0 | 4
| 26 | 10
| 4 | 11
| 4 | 11
| 26 | 52
| 4 | 3
| 4 | 8
| 8 | 41
| 12 | 59
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 2
| 0 | 3
| 0 | 2
| 0 | 0
| 0 | 6
| 0 | 4
| 0 | 3
| 0 | 0
| 7 | 0
| 13 | 0
| 6 | 11
| 2 | 23
| 0 | 12
| 12552 | 17070
| 17 | 26
| 6 | 12
| 4 | 8
| 2 | 9
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 2
| 0 | 0
| 0 | 0
| 2 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 1 | 0
| 0 | 0
| 2 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 2
| 0 | 1
| 4 | 4
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 6
| 0 | 0
| 1 | 0
| 0 | 1
| 0 | 0
| 0 | 0
| 0 | 0
| 1 | 0
| 0 | 0
| 0 | 2
| 0 | 2
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 1 | 0
| 2 | 0
| 0 | 2
| 0 | 0
| 0 | 4
| 0 | 0
| 0 | 3
| 6 | 0
| 0 | 0
| 0 | 5
| 8 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 2
| 0 | 3
| 0 | 2
| 0 | 0
| 3 | 4
| 0 | 0
| 1 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 5
| 1 | 4
| 0 | 0
| 0 | 0
| 3 | 0
| 3 | 0
| 1 | 5
| 0 | 3
| 0 | 2
| 0 | 2
| 0 | 0
| 0 | 5
| 0 | 2
| 2 | 0
| 0 | 0
| 0 | 0
| 2 | 2
| 3 | 9
| 0 | 4
| 0 | 5
| 2 | 6
| 1 | 2
| 0 | 0
| 0 | 0
| 8 | 0
| 2 | 0
| 3 | 0
| 0 | 1
| 0 | 8
| 0 | 3
| 0 | 5
| 1 | 5
| 0 | 0
| 0 | 0
| 0 | 0
Run Gas Calculations
Run Gas Ratio Calculations

## Ethylene-Ethane Results
IEEE Std C57.139-2010 Guide for Dissolved Gas Analysis in Transformer Load Tap Changers Statistics Calculator
| Ethylene | Ethane | Variable | Formula | Ratio of Gas 1 / Gas 2 | Original Ratio of Gas 1 / Gas 2 | LN Ratio of Gas 1 / Gas 2 | Variable | Formula
| #N/A | 0 | Q1 | =QUARTILE(Range,1) | #N/A | 3.4261 | 43 | N | =COUNT(Range LN))
| #N/A | 0 | MEDIAN | =MEDIAN(Range) |  |  | 1.6258 | Avg | =AVERAGE(Range LN)
| #N/A | 2 | Q3 | =QUARTILE(Range,3) | #N/A | 9.1308 | 0.88551 | StdDev | =STDEV(Range LN)
| #N/A | 2 | IQR | =Q3 - Q1 | #N/A | 5.7046 | 21.9078 | C0.95 | =EXP(Avg+1.65*StdDev) CAUTION LIMIT
|  |  | U1 | =Q3 + IQR*1.5 | #N/A | 17.6877 | 40.0045 | C0.99 | =EXP(Avg+2.33*StdDev) WARNING LIMIT
| #N/A | 8 | U2 | =Q3 + IQR*3 | #N/A | 26.2447 | 29.8676 | C??? | =EXP(Avg+???*StdDev) USER DEFINED LIMIT
| ^ CAUTION LIMITS ^ | [6 empty] | 2 | User Defined Tolerance Bounds
|  |  | 1. Choose the two gases for analysis |  |  |  | 12.7647 | C0.85 | User Selected LogNormal Percentile
|  |  | 2. Click Run Gas Calculations button |  |  |  | 78.4122 | C0.999 | User Selected LogNormal Percentile
3. Click Run Gas Ratio Calculations button
| C2H4 | C2H6 | 4. (Optional) Enter User Defined Tolerance Bounds or Select Percentiles for Ratio Calculations
| Gas 1 | Gas 2 |  |  | 44
| Ethylene | Ethane |  |  | Gas 1 / Gas 2 | LN (Gas1 / Gas2)
| 0 | 726 | Total Values |  | 0 | 8
| 4 | 0 |  |  | 4.9333 | 1.596
| 5 | 7 |  |  | 11.6 | 2.451
| 3 | 0 |  |  | 16.3333 | 2.7932
| 0 | 0 |  |  | 14.7 | 2.6878
| 0 | 0 |  |  | 14.2982 | 2.6601
| 0 | 0 |  |  | 1.75 | 0.55962
| 11 | 0 |  |  | 4.5833 | 1.5224
| 0 | 0 |  |  | 7.3881 | 1.9999
| 2 | 5 |  |  | 7.5408 | 2.0203
| 0 | 0 |  |  | 5.8671 | 1.7694
| 0 | 0 |  |  | 6.0634 | 1.8023
| 0 | 0 |  |  | 6.1776 | 1.8209
| 1 | 1 |  |  | 2 | 0.69315
| 0 | 0 |  |  | 0.91667 | -0.087011
| 0 | 0 |  |  | 7.813 | 2.0558
| 0 | 0 |  |  | 6.3501 | 1.8485
| 74 | 15 |  |  | 7.0713 | 1.956
| 3 | 0 |  |  | 6.046 | 1.7994
| 6 | 0 |  |  | 6.2213 | 1.828
| 7 | 0 |  |  | 5.3994 | 1.6863
| 3 | 0 |  |  | 0.83333 | -0.18232
| 1 | 0 |  |  | 13.7 | 2.6174
| 4 | 0 |  |  | 14.6667 | 2.6856
| 3 | 0 |  |  | 7 | 1.9459
| 5 | 0 |  |  | 13.3571 | 2.5921
| 4 | 0 |  |  | 20.1111 | 3.0013
| 4 | 0 |  |  | 4.16 | 1.4255
| 3 | 0 |  |  | 17.4375 | 2.8586
| 4 | 0 |  |  | 3.4375 | 1.2347
| 4 | 0 |  |  | 1.3288 | 0.28425
| 4 | 0 |  |  | 0.83333 | -0.18232
| 2 | 0 |  |  | 3.5 | 1.2528
| 5 | 0 |  |  | 2.5455 | 0.93431
| 4 | 0 |  |  | 3.4444 | 1.2368
| 2 | 0 |  |  | 1.2667 | 0.23639
| 0 | 0 |  |  | 3.6533 | 1.2956
| 1 | 0 |  |  | 7.325 | 1.9913
| 0 | 0 |  |  | 1.0769 | 0.074108
| 0 | 5 |  |  | 8.3077 | 2.1172
| 1 | 4 |  |  | 18.5 | 2.9178
| 1 | 0 |  |  | 2.7692 | 1.0186
| 1 | 0 |  |  | 3.392 | 1.2214
| 0 | 0 |  |  | 6.4706 | 1.8673
| 28 | 0
| 18 | 0
| 14 | 0
| 50 | 0
| 58 | 4
| 72 | 5
| 64 | 2
| 26 | 1
| 10 | 0
| 10 | 5
| 18 | 2
| 21 | 0
| 5 | 0
| 6 | 0
| 6 | 0
| 1 | 0
| 6 | 0
| 6 | 0
| 7 | 0
| 13 | 0
| 4 | 0
| 0 | 0
| 1 | 0
| 0 | 1
| 0 | 0
| 18 | 0
| 22 | 3
| 15 | 0
| 19 | 3
| 16 | 0
| 20 | 0
| 18 | 0
| 23 | 0
| 19 | 0
| 21 | 0
| 14 | 0
| 12 | 0
| 23 | 0
| 20 | 0
| 14 | 0
| 0 | 0
| 0 | 0
| 8 | 0
| 1 | 2
| 2 | 0
| 38 | 6
| 10 | 0
| 13 | 0
| 3 | 1
| 0 | 0
| 25 | 0
| 4 | 2
| 2 | 0
| 2 | 0
| 48 | 3
| 93 | 5
| 4 | 0
| 30 | 5
| 12 | 0
| 5 | 6
| 0 | 0
| 2 | 0
| 0 | 0
| 5 | 0
| 15 | 3
| 13 | 2
| 10 | 5
| 5 | 4
| 5 | 0
| 3 | 0
| 8 | 0
| 7 | 2
| 4 | 0
| 10 | 4
| 14 | 3
| 0 | 0
| 9 | 0
| 22 | 7
| 6 | 2
| 16 | 3
| 6 | 0
| 5 | 0
| 0 | 0
| 3 | 0
| 6 | 0
| 4 | 0
| 5 | 0
| 8 | 0
| 174 | 15
| 1 | 0
| 83 | 4
| 245 | 15
| 294 | 20
| 815 | 57
| 71 | 5
| 14 | 0
| 7 | 0
| 19 | 0
| 11 | 0
| 16 | 2
| 28 | 16
| 3 | 1
| 4 | 0
| 3 | 0
| 3 | 0
| 4 | 0
| 3 | 1
| 5 | 0
| 8 | 0
| 55 | 12
| 9 | 0
| 10 | 0
| 10 | 6
| 13 | 0
| 7 | 0
| 6 | 0
| 16 | 1
| 13 | 1
| 2 | 0
| 0 | 0
| 3 | 0
| 0 | 1
| 3 | 0
| 7 | 0
| 8 | 0
| 4 | 0
| 11 | 2
| 19 | 0
| 12 | 0
| 18 | 0
| 5 | 0
| 35 | 0
| 0 | 1
| 4 | 0
| 4 | 4
| 2 | 0
| 1 | 0
| 3 | 0
| 2 | 0
| 3731 | 505
| 4434 | 588
| 8343 | 1422
| 10526 | 1736
| 13424 | 2173
| 6 | 0
| 9 | 0
| 10 | 0
| 9 | 7
| 16 | 0
| 10 | 1
| 14 | 0
| 17 | 0
| 8 | 0
| 0 | 0
| 3 | 0
| 17 | 2
| 4 | 0
| 20 | 10
| 15 | 9
| 11 | 12
| 22 | 2
| 11 | 0
| 7 | 0
| 10 | 0
| 8 | 0
| 6 | 0
| 22 | 0
| 10 | 0
| 4 | 0
| 3 | 0
| 9 | 0
| 8 | 0
| 13 | 0
| 11 | 0
| 5 | 0
| 12 | 0
| 27 | 3
| 3969 | 508
| 2 | 0
| 2 | 0
| 0 | 0
| 1 | 4
| 1 | 0
| 2 | 0
| 1 | 0
| 3 | 0
| 8 | 0
| 7 | 0
| 8 | 0
| 23 | 0
| 8 | 0
| 14 | 0
| 5 | 0
| 18 | 3
| 7 | 2
| 18 | 4
| 26 | 0
| 11 | 0
| 19 | 1
| 9 | 0
| 10 | 0
| 0 | 0
| 6 | 2
| 6 | 3
| 5 | 0
| 9 | 0
| 0 | 0
| 5 | 0
| 3 | 0
| 2 | 1
| 2 | 0
| 2 | 0
| 0 | 0
| 10 | 0
| 8 | 0
| 3 | 0
| 2 | 0
| 0 | 0
| 3 | 0
| 1 | 0
| 19 | 7
| 15 | 1
| 8 | 0
| 17 | 0
| 0 | 0
| 5 | 0
| 3 | 0
| 2 | 0
| 1 | 0
| 0 | 3
| 7709 | 1214
| 8733 | 1235
| 12346 | 2042
| 14 | 9
| 0 | 0
| 32 | 7
| 11 | 0
| 17 | 0
| 22 | 0
| 1 | 1
| 6 | 0
| 7 | 0
| 11 | 0
| 4 | 0
| 5 | 0
| 4 | 3
| 6 | 0
| 11833 | 1902
| 8504 | 1575
| 9 | 1
| 10 | 12
| 10 | 2
| 13 | 0
| 14 | 0
| 10 | 0
| 14 | 0
| 9 | 2
| 7 | 0
| 8 | 0
| 6 | 0
| 9 | 0
| 6 | 0
| 6 | 0
| 137 | 10
| 5 | 0
| 3 | 0
| 17 | 0
| 8 | 0
| 11 | 0
| 8 | 2
| 9 | 0
| 14 | 0
| 17 | 0
| 12 | 0
| 4 | 0
| 4 | 0
| 6 | 0
| 4 | 7
| 4 | 0
| 6 | 0
| 7 | 0
| 308 | 21
| 14 | 1
| 14 | 0
| 14 | 0
| 19 | 0
| 19 | 0
| 17 | 0
| 16 | 0
| 7 | 0
| 8 | 0
| 14 | 0
| 10 | 0
| 9 | 0
| 8 | 2
| 14 | 0
| 6 | 3
| 31 | 8
| 5 | 3
| 5 | 0
| 6 | 5
| 2 | 0
| 18 | 0
| 1 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 6 | 0
| 3 | 3
| 0 | 0
| 20 | 3
| 5 | 0
| 2 | 7
| 0 | 0
| 10 | 0
| 1 | 0
| 2 | 0
| 0 | 3
| 0 | 0
| 0 | 0
| 32 | 6
| 36 | 3
| 1 | 1
| 7 | 0
| 70 | 10
| 25 | 5
| 0 | 0
| 0 | 0
| 0 | 0
| 4 | 1
| 0 | 0
| 0 | 0
| 0 | 0
| 94 | 3
| 187 | 14
| 362 | 18
| 104 | 25
| 48 | 6
| 7 | 0
| 15 | 0
| 10 | 0
| 8 | 0
| 21 | 0
| 7 | 4
| 12 | 1
| 14 | 0
| 15 | 0
| 12 | 0
| 33 | 1
| 11 | 0
| 24 | 1
| 27 | 0
| 16 | 2
| 29 | 0
| 3 | 0
| 60 | 6
| 20 | 0
| 308 | 11
| 279 | 16
| 31 | 3
| 55 | 16
| 58 | 3
| 76 | 5
| 97 | 73
| 65 | 78
| 40 | 4
| 16 | 3
| 5 | 0
| 5 | 0
| 6 | 2
| 12 | 0
| 12 | 0
| 0 | 1
| 1 | 1
| 13 | 6
| 9 | 0
| 0 | 0
| 2 | 0
| 0 | 0
| 0 | 0
| 11 | 0
| 15 | 6
| 14 | 0
| 8 | 0
| 11 | 2
| 12 | 3
| 0 | 0
| 0 | 0
| 8 | 0
| 1 | 0
| 4 | 0
| 3 | 0
| 5 | 6
| 1 | 2
| 2 | 3
| 0 | 0
| 11 | 0
| 4 | 0
| 7 | 0
| 7 | 0
| 4 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 3 | 0
| 0 | 0
| 0 | 0
| 2 | 0
| 9 | 3
| 8 | 0
| 9 | 0
| 9 | 3
| 3 | 0
| 6 | 0
| 7 | 2
| 8 | 1
| 2 | 0
| 4 | 0
| 10 | 0
| 6 | 0
| 5 | 0
| 8 | 0
| 10 | 0
| 2 | 0
| 3 | 0
| 0 | 0
| 11 | 0
| 2 | 1
| 0 | 0
| 3 | 0
| 0 | 0
| 0 | 0
| 2 | 0
| 2 | 0
| 3 | 0
| 0 | 0
| 3 | 0
| 14 | 1
| 7 | 0
| 8 | 0
| 6 | 0
| 0 | 3
| 4 | 0
| 7 | 0
| 4 | 1
| 2 | 1
| 0 | 0
| 8 | 0
| 6 | 0
| 8 | 3
| 4 | 0
| 4 | 0
| 7 | 0
| 2 | 4
| 3 | 0
| 0 | 0
| 2 | 0
| 4 | 0
| 4 | 2
| 4 | 10
| 5 | 0
| 26 | 6
| 3 | 0
| 0 | 0
| 3 | 7
| 42 | 12
| 25 | 0
| 28 | 11
| 22 | 3
| 6 | 0
| 9 | 0
| 19 | 0
| 7 | 0
| 5 | 0
| 5 | 1
| 16 | 4
| 5 | 0
| 15 | 5
| 10 | 0
| 10 | 0
| 13 | 0
| 6 | 0
| 17 | 3
| 9 | 1
| 7 | 0
| 11 | 2
| 13 | 0
| 8 | 0
| 20 | 0
| 8 | 0
| 6 | 0
| 0 | 0
| 6 | 0
| 4 | 0
| 6 | 0
| 4 | 0
| 69 | 4
| 0 | 0
| 62 | 18
| 42 | 7
| 9 | 2
| 13 | 0
| 19 | 15
| 12 | 0
| 11 | 0
| 8 | 0
| 10 | 2
| 7 | 0
| 6 | 0
| 7 | 0
| 0 | 0
| 0 | 0
| 1 | 1
| 2 | 0
| 6 | 3
| 5 | 0
| 6 | 0
| 4 | 3
| 31 | 3
| 8 | 0
| 0 | 1
| 0 | 0
| 0 | 0
| 0 | 0
| 6 | 2
| 3 | 0
| 13 | 0
| 5 | 0
| 274 | 75
| 20 | 3
| 293 | 40
| 4 | 7
| 6 | 0
| 0 | 0
| 2 | 0
| 2 | 0
| 1 | 0
| 1 | 0
| 2 | 0
| 9 | 0
| 57 | 6
| 58 | 5
| 32 | 0
| 29 | 2
| 25 | 0
| 28 | 26
| 49 | 4
| 49 | 4
| 216 | 26
| 29 | 4
| 41 | 4
| 138 | 8
| 222 | 12
| 10 | 0
| 4 | 0
| 3 | 0
| 3 | 0
| 0 | 0
| 2 | 0
| 4 | 0
| 8 | 0
| 2 | 0
| 0 | 0
| 0 | 0
| 45 | 7
| 36 | 13
| 38 | 6
| 28 | 2
| 30 | 0
| 42577 | 12552
| 110 | 17
| 44 | 6
| 40 | 4
| 36 | 2
| 7 | 0
| 4 | 0
| 6 | 0
| 8 | 0
| 5 | 0
| 4 | 0
| 0 | 0
| 2 | 0
| 0 | 2
| 3 | 0
| 0 | 0
| 0 | 0
| 11 | 1
| 7 | 0
| 8 | 2
| 7 | 0
| 0 | 0
| 5 | 0
| 0 | 0
| 1 | 0
| 2 | 0
| 0 | 0
| 2 | 0
| 9 | 0
| 8 | 0
| 8 | 0
| 5 | 0
| 29 | 4
| 4 | 0
| 0 | 0
| 3 | 0
| 6 | 0
| 4 | 0
| 6 | 1
| 5 | 0
| 4 | 0
| 12 | 0
| 6 | 0
| 9 | 1
| 5 | 0
| 6 | 0
| 5 | 0
| 0 | 0
| 1 | 0
| 3 | 0
| 2 | 0
| 0 | 0
| 7 | 0
| 2 | 1
| 13 | 2
| 4 | 0
| 2 | 0
| 2 | 0
| 2 | 0
| 5 | 0
| 12 | 6
| 6 | 0
| 18 | 0
| 20 | 8
| 0 | 0
| 3 | 0
| 11 | 0
| 15 | 0
| 6 | 0
| 11 | 0
| 4 | 0
| 13 | 0
| 4 | 3
| 0 | 0
| 4 | 1
| 0 | 0
| 4 | 0
| 3 | 0
| 7 | 0
| 23 | 1
| 14 | 0
| 6 | 0
| 6 | 3
| 3 | 3
| 7 | 1
| 5 | 0
| 5 | 0
| 3 | 0
| 3 | 0
| 13 | 0
| 3 | 0
| 42 | 2
| 12 | 0
| 12 | 0
| 13 | 2
| 17 | 3
| 7 | 0
| 9 | 0
| 11 | 2
| 6 | 1
| 3 | 0
| 4 | 0
| 39 | 8
| 8 | 2
| 9 | 3
| 10 | 0
| 13 | 0
| 7 | 0
| 7 | 0
| 10 | 1
| 3 | 0
| 3 | 0
| 0 | 0
Run Gas Calculations
Run Gas Ratio Calculations

## Methane-Acetylene Results
IEEE Std C57.139-2010 Guide for Dissolved Gas Analysis in Transformer Load Tap Changers Statistics Calculator
| Methane | Acetylene | Variable | Formula | Ratio of Gas 1 / Gas 2 | Original Ratio of Gas 1 / Gas 2 | LN Ratio of Gas 1 / Gas 2 | Variable | Formula
| #N/A | 11.25 | Q1 | =QUARTILE(Range,1) | #N/A | 0.061856 | 57 | N | =COUNT(Range LN))
| #N/A | 35 | MEDIAN | =MEDIAN(Range) |  |  | -2.4409 | Avg | =AVERAGE(Range LN)
| #N/A | 64.75 | Q3 | =QUARTILE(Range,3) | #N/A | 0.47931 | 0.87415 | StdDev | =STDEV(Range LN)
| #N/A | 53.5 | IQR | =Q3 - Q1 | #N/A | 0.41745 | 0.36843 | C0.95 | =EXP(Avg+1.65*StdDev) CAUTION LIMIT
|  |  | U1 | =Q3 + IQR*1.5 | #N/A | 1.1055 | 0.66759 | C0.99 | =EXP(Avg+2.33*StdDev) WARNING LIMIT
| #N/A | 225.25 | U2 | =Q3 + IQR*3 | #N/A | 1.7317 | 0.5003 | C??? | =EXP(Avg+???*StdDev) USER DEFINED LIMIT
| ^ CAUTION LIMITS ^ | [6 empty] | 2 | User Defined Tolerance Bounds
|  |  | 1. Choose the two gases for analysis |  |  |  | 0.21616 | C0.85 | User Selected LogNormal Percentile
|  |  | 2. Click Run Gas Calculations button |  |  |  | 1.2973 | C0.999 | User Selected LogNormal Percentile
3. Click Run Gas Ratio Calculations button
| CH4 | C2H2 | 4. (Optional) Enter User Defined Tolerance Bounds or Select Percentiles for Ratio Calculations
| Gas 1 | Gas 2 |  |  | 71
| Methane | Acetylene |  |  | Gas 1 / Gas 2 | LN (Gas1 / Gas2)
| 0 | 8 | Total Values |  | 0 | 8
| 0 | 38 |  |  | 0.099415 | -2.3085
| 1 | 19 |  |  | 0.06264 | -2.7704
| 2 | 25 |  |  | 0.041391 | -3.1847
| 0 | 17 |  |  | 0.035573 | -3.3362
| 2 | 20 |  |  | 0.059524 | -2.8214
| 0 | 24 |  |  | 0.1028 | -2.2749
| 0 | 29 |  |  | 0.084507 | -2.4709
| 0 | 10 |  |  | 1.3828 | 0.32412
| 0 | 0 |  |  | 0.022398 | -3.7988
| 2 | 0 |  |  | 0.13158 | -2.0281
| 0 | 0 |  |  | 0.11236 | -2.1861
| 0 | 0 |  |  | 0.050542 | -2.985
| 0 | 0 |  |  | 0.097826 | -2.3246
| 0 | 0 |  |  | 0.066089 | -2.7168
| 0 | 0 |  |  | 0.068392 | -2.6825
| 0 | 0 |  |  | 0.073789 | -2.6065
| 0 | 40 |  |  | 0.087179 | -2.4398
| 0 | 23 |  |  | 0.092105 | -2.3848
| 0 | 57 |  |  | 0.090278 | -2.4049
| 0 | 19 |  |  | 0.2 | -1.6094
| 1 | 26 |  |  | 0.073171 | -2.615
| 0 | 21 |  |  | 0.125 | -2.0794
| 1 | 25 |  |  | 1.2703 | 0.23923
| 0 | 26 |  |  | 0.10101 | -2.2925
| 0 | 30 |  |  | 0.089041 | -2.4187
| 0 | 32 |  |  | 0.14433 | -1.9357
| 0 | 42 |  |  | 0.12624 | -2.0696
| 0 | 17 |  |  | 1.5294 | 0.42488
| 0 | 18 |  |  | 0.056528 | -2.873
| 2 | 30 |  |  | 0.10976 | -2.2095
| 0 | 18 |  |  | 0.12997 | -2.0404
| 1 | 42 |  |  | 0.074074 | -2.6027
| 0 | 36 |  |  | 0.081301 | -2.5096
| 0 | 26 |  |  | 0.018519 | -3.989
| 0 | 14 |  |  | 0.01737 | -4.053
| 0 | 10 |  |  | 0.087838 | -2.4323
| 0 | 9 |  |  | 0.061856 | -2.783
| 0 | 9 |  |  | 0.054422 | -2.911
| 0 | 0 |  |  | 0.033482 | -3.3967
| 2 | 0 |  |  | 0.05 | -2.9957
| 0 | 7 |  |  | 0.75862 | -0.27625
| 0 | 0 |  |  | 0.12741 | -2.0603
| 0 | 0 |  |  | 0.073298 | -2.6132
| 0 | 238 |  |  | 0.094059 | -2.3638
| 5 | 144 |  |  | 0.093333 | -2.3716
| 17 | 171 |  |  | 0.045652 | -3.0867
| 28 | 447 |  |  | 0.077519 | -2.5572
| 23 | 5.2 |  |  | 0.06962 | -2.6647
| 25 | 604 |  |  | 0.061453 | -2.7895
| 18 | 506 |  |  | 0.094033 | -2.3641
| 4 | 100 |  |  | 0.051702 | -2.9623
| 0 | 102 |  |  | 0.044428 | -3.1139
| 0 | 69 |  |  | 0.055 | -2.9004
| 10 | 168 |  |  | 0.14557 | -1.9271
| 5 | 60 |  |  | 0.04428 | -3.1172
| 3 | 55 |  |  | 0.072423 | -2.6252
| 2 | 45 |  |  | 0.061856 | -2.783
| 0 | 38
| 0 | 47
| 2 | 44
| 0 | 36
| 0 | 55
| 6 | 69
| 2 | 24
| 0 | 0
| 0 | 4
| 0 | 6
| 1 | 0
| 0 | 157
| 0 | 145
| 0 | 97
| 4 | 115
| 6 | 131
| 9 | 150
| 7 | 161
| 11 | 107
| 5 | 121
| 6 | 171
| 4 | 87
| 5 | 6
| 0 | 73
| 6 | 128
| 3 | 101
| 0 | 0
| 0 | 16
| 0 | 79
| 0 | 13
| 3 | 0
| 0 | 410
| 5 | 110
| 4 | 143
| 0 | 16
| 0 | 11
| 12 | 142
| 2 | 17
| 0 | 14
| 0 | 9
| 531 | 384
| 17 | 759
| 0 | 60
| 20 | 152
| 3 | 76
| 2 | 31
| 0 | 0
| 0 | 0
| 0 | 0
| 4 | 24
| 0 | 104
| 0 | 82
| 0 | 54
| 0 | 41
| 0 | 8
| 0 | 22
| 0 | 34
| 0 | 26
| 0 | 6
| 0 | 33
| 8 | 38
| 0 | 0
| 0 | 51
| 20 | 178
| 1 | 38
| 6 | 102
| 0 | 43
| 3 | 22
| 0 | 7
| 2 | 14
| 0 | 19
| 0 | 29
| 0 | 20
| 0 | 38
| 28 | 554
| 14 | 0
| 36 | 368
| 61 | 923
| 74 | 1082
| 192 | 2602
| 34 | 390
| 0 | 73
| 0 | 53
| 14 | 152
| 4 | 60
| 4 | 101
| 13 | 144
| 2 | 15
| 0 | 16
| 2 | 43
| 0 | 27
| 1 | 2
| 0 | 21
| 0 | 28
| 7 | 37
| 0 | 34
| 0 | 38
| 0 | 43
| 0 | 43
| 0 | 37
| 3 | 56
| 2 | 31
| 4 | 81
| 7 | 60
| 0 | 11
| 0 | 5
| 0 | 12
| 0 | 18
| 3 | 17
| 0 | 38
| 0 | 39
| 0 | 29
| 3 | 76
| 8 | 158
| 6 | 98
| 6 | 117
| 4 | 44
| 3 | 35
| 0 | 9
| 0 | 26
| 0 | 28
| 0 | 30
| 0 | 1
| 0 | 16
| 2 | 15
| 1833 | 149
| 2026 | 163
| 3802 | 211
| 4449 | 274
| 5440 | 360
| 0 | 36
| 0 | 56
| 0 | 48
| 0 | 30
| 5 | 80
| 2 | 58
| 3 | 62
| 4 | 43
| 3 | 35
| 0 | 0
| 0 | 9
| 0 | 51
| 2 | 12
| 0 | 119
| 0 | 102
| 10 | 50
| 12 | 164
| 4 | 82
| 5 | 50
| 5 | 65
| 3 | 50
| 5 | 68
| 13 | 104
| 4 | 66
| 3 | 22
| 2 | 20
| 0 | 63
| 0 | 36
| 5 | 67
| 0 | 37
| 0 | 30
| 4 | 42
| 47 | 37
| 1366 | 263
| 0 | 9
| 0 | 17
| 0 | 0
| 0 | 0
| 0 | 9
| 0 | 10
| 0 | 6
| 0 | 4
| 0 | 56
| 0 | 53
| 0 | 57
| 0 | 73
| 0 | 64
| 4 | 68
| 2 | 40
| 5 | 44
| 3 | 46
| 10 | 99
| 13 | 146
| 2 | 35
| 6 | 90
| 6 | 46
| 4 | 42
| 0 | 0
| 0 | 34
| 0 | 22
| 0 | 39
| 4 | 49
| 0 | 28
| 4 | 61
| 0 | 21
| 0 | 2
| 0 | 6
| 0 | 4
| 4 | 4
| 0 | 14
| 0 | 12
| 0 | 9
| 0 | 4
| 3 | 0
| 0 | 3
| 0 | 22
| 0 | 120
| 8 | 118
| 4 | 86
| 4 | 98
| 0 | 5
| 2 | 49
| 7 | 13
| 0 | 14
| 0 | 0
| 0 | 0
| 2794 | 222
| 2952 | 301
| 4520 | 426
| 0 | 7
| 0 | 0
| 0 | 45
| 0 | 23
| 0 | 76
| 6 | 93
| 0 | 0
| 0 | 42
| 1 | 9
| 2 | 41
| 0 | 14
| 0 | 31
| 0 | 0
| 0 | 28
| 5450 | 374
| 4474 | 243
| 0 | 73
| 0 | 43
| 0 | 54
| 0 | 61
| 9 | 108
| 0 | 40
| 4 | 68
| 0 | 55
| 3 | 47
| 3 | 23
| 0 | 33
| 0 | 45
| 4 | 36
| 6 | 0
| 56 | 388
| 3 | 5
| 2 | 14
| 0 | 46
| 0 | 35
| 0 | 39
| 0 | 48
| 0 | 40
| 3 | 55
| 0 | 79
| 0 | 43
| 1 | 11
| 0 | 15
| 1 | 25
| 3 | 0
| 0 | 24
| 4 | 25
| 4 | 24
| 166 | 1315
| 5 | 27
| 0 | 77
| 0 | 97
| 0 | 154
| 0 | 186
| 0 | 124
| 3 | 68
| 1 | 37
| 0 | 49
| 9 | 82
| 6 | 59
| 4 | 39
| 5 | 37
| 5 | 55
| 0 | 33
| 0 | 31
| 0 | 34
| 4 | 33
| 16 | 0
| 0 | 15
| 8 | 155
| 0 | 1
| 0 | 2
| 0 | 0
| 0 | 0
| 0 | 41
| 0 | 28
| 0 | 24
| 26 | 17
| 0 | 38
| 13 | 0
| 0 | 10
| 5 | 81
| 0 | 5
| 0 | 3
| 0 | 7
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 45 | 0
| 14 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 42 | 743
| 162 | 1476
| 353 | 2716
| 0 | 139
| 0 | 333
| 0 | 44
| 0 | 76
| 0 | 67
| 0 | 59
| 10 | 135
| 3 | 48
| 0 | 68
| 4 | 17
| 3 | 75
| 0 | 46
| 10 | 123
| 0 | 252
| 4 | 81
| 6 | 113
| 3 | 72
| 3 | 86
| 0 | 0
| 0 | 153
| 0 | 0
| 35 | 1890
| 28 | 1612
| 0 | 153
| 13 | 148
| 12 | 194
| 24 | 441
| 15 | 448
| 11 | 220
| 4 | 1
| 0 | 53
| 0 | 19
| 0 | 21
| 2 | 8
| 2 | 35
| 0 | 13
| 0 | 0
| 0 | 18
| 7 | 125
| 3 | 66
| 0 | 3
| 0 | 5
| 0 | 8
| 0 | 9
| 0 | 89
| 0 | 57
| 5 | 77
| 0 | 68
| 4 | 30
| 2 | 12
| 0 | 0
| 0 | 0
| 5 | 25
| 0 | 0
| 0 | 19
| 0 | 24
| 0 | 26
| 0 | 0
| 0 | 0
| 0 | 0
| 2 | 45
| 0 | 21
| 0 | 36
| 0 | 23
| 3 | 22
| 0 | 14
| 0 | 0
| 0 | 4
| 0 | 8
| 0 | 13
| 0 | 14
| 0 | 8
| 0 | 12
| 0 | 50
| 0 | 37
| 0 | 53
| 0 | 60
| 0 | 10
| 3 | 47
| 2 | 53
| 5 | 42
| 0 | 22
| 6 | 36
| 5 | 77
| 3 | 36
| 4 | 32
| 0 | 36
| 0 | 13
| 0 | 4
| 0 | 24
| 0 | 18
| 3 | 25
| 0 | 36
| 0 | 1
| 0 | 16
| 0 | 1
| 0 | 0
| 0 | 0
| 0 | 11
| 0 | 11
| 0 | 0
| 0 | 18
| 0 | 41
| 0 | 54
| 9 | 80
| 0 | 46
| 1 | 7
| 2 | 24
| 0 | 13
| 0 | 11
| 0 | 2
| 0 | 0
| 0 | 68
| 0 | 36
| 0 | 43
| 0 | 36
| 0 | 42
| 1 | 27
| 0 | 12
| 0 | 16
| 0 | 0
| 2 | 21
| 0 | 36
| 2 | 38
| 22 | 29
| 0 | 42
| 4 | 36
| 0 | 12
| 0 | 0
| 0 | 0
| 33 | 259
| 14 | 191
| 19 | 202
| 14 | 150
| 2 | 37
| 2 | 41
| 3 | 52
| 0 | 32
| 0 | 22
| 0 | 20
| 0 | 74
| 0 | 29
| 0 | 58
| 0 | 71
| 0 | 62
| 3 | 59
| 1 | 30
| 5 | 68
| 7 | 50
| 4 | 45
| 6 | 49
| 0 | 86
| 0 | 57
| 0 | 75
| 1 | 40
| 3 | 28
| 0 | 3
| 0 | 32
| 2 | 21
| 2 | 32
| 1 | 1
| 21 | 460
| 2 | 0
| 10 | 5
| 0 | 82
| 0 | 43
| 0 | 84
| 0 | 151
| 8 | 95
| 0 | 70
| 0 | 67
| 5 | 52
| 3 | 45
| 3 | 40
| 2 | 29
| 0 | 6
| 0 | 9
| 2 | 0
| 0 | 9
| 0 | 40
| 0 | 35
| 0 | 46
| 0 | 26
| 4 | 29
| 4 | 41
| 0 | 1
| 0 | 0
| 0 | 0
| 0 | 4
| 0 | 0
| 0 | 0
| 0 | 95
| 0 | 30
| 258 | 16
| 0 | 51
| 126 | 72
| 5 | 29
| 3 | 29
| 0 | 5
| 1 | 7
| 0 | 10
| 0 | 1
| 0 | 0
| 1 | 47
| 0 | 6
| 0 | 259
| 0 | 269
| 0 | 151
| 6 | 130
| 4 | 148
| 10 | 129
| 11 | 158
| 11 | 179
| 52 | 553
| 3 | 13
| 8 | 120
| 41 | 793
| 59 | 1328
| 0 | 57
| 0 | 17
| 0 | 11
| 2 | 0
| 3 | 21
| 2 | 14
| 0 | 16
| 6 | 12
| 4 | 2
| 3 | 0
| 0 | 0
| 0 | 2239
| 0 | 181
| 11 | 200
| 23 | 158
| 12 | 271
| 17070 | 630
| 26 | 359
| 12 | 194
| 8 | 161
| 9 | 146
| 0 | 25
| 0 | 45
| 0 | 35
| 0 | 39
| 0 | 27
| 2 | 30
| 0 | 8
| 0 | 6
| 0 | 8
| 0 | 22
| 0 | 8
| 0 | 4
| 0 | 47
| 0 | 45
| 0 | 50
| 0 | 47
| 0 | 26
| 0 | 24
| 0 | 0
| 0 | 8
| 0 | 6
| 0 | 4
| 0 | 8
| 0 | 58
| 0 | 49
| 2 | 48
| 1 | 38
| 4 | 44
| 0 | 37
| 0 | 14
| 0 | 6
| 6 | 5
| 0 | 14
| 0 | 20
| 1 | 22
| 0 | 12
| 0 | 86
| 0 | 32
| 0 | 45
| 0 | 43
| 2 | 73
| 2 | 43
| 0 | 8
| 0 | 21
| 0 | 7
| 0 | 1
| 0 | 0
| 0 | 37
| 0 | 12
| 0 | 39
| 2 | 19
| 0 | 24
| 4 | 12
| 0 | 18
| 3 | 23
| 0 | 52
| 0 | 43
| 5 | 104
| 0 | 51
| 0 | 0
| 0 | 11
| 0 | 56
| 0 | 43
| 2 | 58
| 3 | 56
| 2 | 50
| 0 | 50
| 4 | 34
| 0 | 6
| 0 | 13
| 0 | 0
| 0 | 12
| 0 | 8
| 5 | 7
| 4 | 1
| 0 | 66
| 0 | 45
| 0 | 45
| 0 | 30
| 5 | 49
| 3 | 31
| 2 | 40
| 2 | 20
| 0 | 25
| 5 | 36
| 2 | 28
| 0 | 180
| 0 | 58
| 0 | 63
| 2 | 66
| 9 | 90
| 4 | 0
| 5 | 62
| 6 | 81
| 2 | 36
| 0 | 1
| 0 | 28
| 0 | 151
| 0 | 31
| 0 | 44
| 1 | 34
| 8 | 60
| 3 | 0
| 5 | 58
| 5 | 52
| 0 | 30
| 0 | 20
| 0 | 0
Run Gas Calculations
Run Gas Ratio Calculations

## Ref
IEEE Std No: | C57.139 | Std
Year: | 2010 | YearPub
Title: | Guide for Dissolved Gas Analysis in Transformer Load Tap Changers | Title
Reference Data
Generic LTC Type Classifications
Contacts
Cont
A | Arcing Contacts
V | Vacuum Contacts
Impedance
Imp
R | Resistor Type
X | Reactor Type
Compartment
Comp
S | Arcing switches in Separate compartment from non-arcing switches
A | One compartment: arcing type selector
N | One compartment: non-arcing type selector
TankSeal
Tank
S | Sealed Tank: with/without pressure relief
B | Non-sealed Tank
Gases
GasName | GasFormula
Hydrogen | H2
Methane | CH4
Ethane | C2H6
Ethylene | C2H4
Acetylene | C2H2
TDHG | TDHG
TolBounds
Percentile
C0.85 | 1.04
C0.90 | 1.28
C0.95 | 1.65
C0.98 | 2.05
C0.99 | 2.33
C0.999 | 3.09

## Ethylene-Acetylene 2BDeleted (hidden)
IEEE Std C57.139-2010 Guide for Dissolved Gas Analysis in Transformer Load Tap Changers Statistics Calculator
| Ethylene | Acetylene | Variable | Formula | Ratio of C2H4/C2H2 | Original Ratio of C2H4/C2H2 | LN Ratio of C2H4/C2H2 | Variable | Formula
| #N/A | 11.25 | Q1 | =QUARTILE(Range,1) | #N/A | 0.21308 | 216 | N | =COUNT(Range LN))
| #N/A | 35 | MEDIAN | =MEDIAN(Range) |  |  | -1.2926 | Avg | =AVERAGE(Range LN)
| #N/A | 64.75 | Q3 | =QUARTILE(Range,3) | #N/A | 0.40628 | 0.4475 | StdDev | =STDEV(Range LN)
| #N/A | 53.5 | IQR | =Q3 - Q1 | #N/A | 0.19321 | 0.57452 | C095 | =EXP(Avg+1.65*StdDev) CAUTION LIMIT
|  |  | U1 | =Q3 + IQR*1.5 | #N/A | 0.69609 | 0.77886 | C099 | =EXP(Avg+2.33*StdDev) WARNING LIMIT
CAUTION LIMIT | #N/A | 225.25 | U2 | =Q3 + IQR*3 | #N/A | 0.9859 | 0.67193 | C??? | =EXP(Avg+???*StdDev) USER DEFINED LIMIT
[8 empty] | 2 | User Defined Band
| Gas 1 | Gas 2 |  |  | 244 |  | 8 | Ratio Final Count
| Ethylene | Acetylene |  |  | Gas 1 / Gas 2 | LN (Gas1 / Gas2) | 2 | Qty >= Ratio Caution Limit
Total Values: | 0 | 8 | Total Values |  | 0 | 8 | 25% | #DIV/0! | % Ratio Caution (of ratios shown & full data set)
Qty Caution: | #N/A | 0 |  |  |  |  | 1 | Qty >= Ratio Warning Limit
% Caution: | #N/A | 0% |  |  |  |  | 12.5% | #DIV/0! | % Ratio Warning (of ratios shown & full data set)
| C2H4 | C2H2 |  |  | C2H4 / C2H2 | Ratio Logs | C2H4 / C2H2 copy
| 4 | 38 |  |  | 0.68421 | -0.37949 | 0.68421
| 5 | 19 |  |  | 0.11765 | -2.1401 | 2.225
| 3 | 25 |  |  | 0.15972 | -1.8343 | 0.11765
| 0 | 17 |  |  | 0.18129 | -1.7077 | 0.15972
| 0 | 20 |  |  | 0.1745 | -1.7458 | 0.18129
| 0 | 24 |  |  | 0.16887 | -1.7786 | 0.1745
| 11 | 29 |  |  | 0.16601 | -1.7957 | 0.16887
| 0 | 10 |  |  | 0.31 | -1.1712 | 0.16601
| 2 | 0 |  |  | 0.21739 | -1.5261 | 0.31
| 0 | 0 |  |  | 0.17857 | -1.7228 | 0.21739
| 0 | 0 |  |  | 0.43333 | -0.83625 | 0.17857
| 0 | 0 |  |  | 0.27536 | -1.2897 | 0.43333
| 1 | 0 |  |  | 0.11465 | -2.1659 | 0.27536
| 0 | 0 |  |  | 0.17241 | -1.7579 | 0.11465
| 0 | 0 |  |  | 0.15464 | -1.8667 | 0.17241
| 0 | 0 |  |  | 0.22609 | -1.4868 | 0.15464
| 74 | 40 |  |  | 0.16794 | -1.7842 | 0.22609
| 3 | 23 |  |  | 0.19333 | -1.6433 | 0.16794
| 6 | 57 |  |  | 0.15528 | -1.8625 | 0.19333
| 7 | 19 |  |  | 0.31776 | -1.1465 | 0.15528
| 3 | 26 |  |  | 0.19835 | -1.6177 | 0.31776
| 1 | 21 |  |  | 0.15789 | -1.8458 | 0.19835
| 4 | 25 |  |  | 0.2069 | -1.5755 | 0.15789
| 3 | 26 |  |  | 0.31507 | -1.155 | 0.2069
| 5 | 30 |  |  | 0.20312 | -1.5939 | 0.31507
| 4 | 32 |  |  | 0.16832 | -1.7819 | 0.20312
| 4 | 42 |  |  | 0.10732 | -2.232 | 0.16832
| 3 | 17 |  |  | 0.13636 | -1.9924 | 0.10732
| 4 | 18 |  |  | 0.11888 | -2.1296 | 0.13636
| 4 | 30 |  |  | 0.26056 | -1.3449 | 0.11888
| 4 | 18 |  |  | 0.15152 | -1.8871 | 0.26056
| 2 | 42 |  |  | 0.36184 | -1.0165 | 1.5156
| 5 | 36 |  |  | 0.19737 | -1.6227 | 0.15152
| 4 | 26 |  |  | 0.41935 | -0.86904 | 0.36184
| 2 | 14 |  |  | 0.17308 | -1.754 | 0.19737
| 0 | 10 |  |  | 0.18293 | -1.6987 | 0.41935
| 1 | 9 |  |  | 0.27778 | -1.2809 | 0.17308
| 0 | 9 |  |  | 0.42424 | -0.85745 | 0.18293
| 0 | 0 |  |  | 0.65789 | -0.41871 | 0.27778
| 1 | 0 |  |  | 0.27528 | -1.29 | 0.42424
| 1 | 7 |  |  | 0.2451 | -1.4061 | 0.65789
| 1 | 0 |  |  | 0.3917 | -0.93727 | 0.27528
| 0 | 0 |  |  | 0.33424 | -1.0959 | 0.2451
| 28 | 238 |  |  | 0.34778 | -1.0562 | 0.3917
| 18 | 144 |  |  | 0.3586 | -1.0256 | 0.33424
| 14 | 171 |  |  | 0.40892 | -0.89424 | 0.34778
| 50 | 447 |  |  | 0.28205 | -1.2657 | 0.3586
| 58 | 5.2 |  |  | 0.19178 | -1.6514 | 0.40892
| 72 | 604 |  |  | 0.21711 | -1.5274 | 0.28205
| 64 | 506 |  |  | 0.25 | -1.3863 | 0.19178
| 26 | 100 |  |  | 0.21782 | -1.5241 | 0.21711
| 10 | 102 |  |  | 0.39583 | -0.92676 | 0.25
| 10 | 69 |  |  | 0.40541 | -0.90287 | 0.21782
| 18 | 168 |  |  | 0.37209 | -0.98861 | 0.39583
| 21 | 60 |  |  | 0.35135 | -1.046 | 0.40541
| 5 | 55 |  |  | 0.25926 | -1.3499 | 1.9706
| 6 | 45 |  |  | 0.35 | -1.0498 | 0.37209
| 6 | 38 |  |  | 0.21053 | -1.5581 | 0.35135
| 1 | 47 |  |  | 0.17089 | -1.7668 | 0.25926
| 6 | 44 |  |  | 0.18367 | -1.6946 | 0.35
| 6 | 36 |  |  | 0.20513 | -1.5841 | 0.21053
| 7 | 55 |  |  | 0.53333 | -0.62861 | 0.17089
| 13 | 69 |  |  | 0.2625 | -1.3375 | 0.18367
| 4 | 24 |  |  | 0.22414 | -1.4955 | 0.20513
| 0 | 0 |  |  | 0.27419 | -1.2939 | 1.0857
| 1 | 4 |  |  | 0.48837 | -0.71668 | 40.7315
| 0 | 6 |  |  | 0.37255 | -0.98739 | 43.2393
| 0 | 0 |  |  | 0.2521 | -1.3779 | 64.2986
| 18 | 157 |  |  | 0.23529 | -1.4469 | 60.9891
| 22 | 145 |  |  | 0.66 | -0.41552 | 58.4361
| 15 | 97 |  |  | 0.21951 | -1.5163 | 0.53333
| 19 | 115 |  |  | 0.18293 | -1.6987 | 0.2625
| 16 | 131 |  |  | 0.23077 | -1.4663 | 0.22414
| 20 | 150 |  |  | 0.33654 | -1.089 | 0.27419
| 18 | 161 |  |  | 0.21212 | -1.5506 | 0.48837
| 23 | 107 |  |  | 0.26866 | -1.3143 | 0.37255
| 19 | 121 |  |  | 0.38095 | -0.96508 | 0.2521
| 21 | 171 |  |  | 0.31507 | -1.155 | 0.23529
| 14 | 87 |  |  | 0.26471 | -1.3291 | 0.66
| 12 | 6 |  |  | 0.59091 | -0.52609 | 0.21951
| 23 | 73 |  |  | 0.32323 | -1.1294 | 0.18293
| 20 | 128 |  |  | 0.26712 | -1.32 | 0.23077
| 14 | 101 |  |  | 0.37143 | -0.9904 | 0.33654
| 0 | 0 |  |  | 0.28889 | -1.2417 | 0.21212
| 0 | 16 |  |  | 0.32609 | -1.1206 | 0.26866
| 8 | 79 |  |  | 0.33333 | -1.0986 | 0.38095
| 1 | 13 |  |  | 0.26531 | -1.3269 | 2.0811
| 2 | 0 |  |  | 0.21667 | -1.5294 | 22.2167
| 38 | 410 |  |  | 0.20339 | -1.5926 | 0.31507
| 10 | 110 |  |  | 0.21429 | -1.5404 | 0.26471
| 13 | 143 |  |  | 0.86667 | -0.1431 | 0.59091
| 3 | 16 |  |  | 0.22368 | -1.4975 | 0.32323
| 0 | 11 |  |  | 0.30108 | -1.2004 | 0.26712
| 25 | 142 |  |  | 0.31707 | -1.1486 | 0.37143
| 4 | 17 |  |  | 0.51163 | -0.67016 | 0.28889
| 2 | 14 |  |  | 0.21311 | -1.5459 | 0.32609
| 2 | 9 |  |  | 0.21296 | -1.5466 | 0.33333
| 48 | 384 |  |  | 0.26471 | -1.3291 | 0.26531
| 93 | 759 |  |  | 0.5232 | -0.6478 | 0.21667
| 4 | 60 |  |  | 0.36957 | -0.99543 | 0.20339
| 30 | 152 |  |  | 0.30909 | -1.1741 | 0.21429
| 12 | 76 |  |  | 0.21519 | -1.5362 | 52.7793
| 5 | 31 |  |  | 0.37643 | -0.97703 | 42.9236
| 0 | 0 |  |  | 0.74074 | -0.3001 | 44.385
| 2 | 0 |  |  | 0.18182 | -1.7047 | 0.86667
| 0 | 0 |  |  | 0.14433 | -1.9357 | 0.22368
| 5 | 24 |  |  | 0.12338 | -2.0925 | 0.30108
| 15 | 104 |  |  | 0.10215 | -2.2813 | 0.31707
| 13 | 82 |  |  | 0.1371 | -1.9871 | 51.2968
| 10 | 54 |  |  | 0.27941 | -1.2751 | 59.8889
| 5 | 41 |  |  | 0.28049 | -1.2712 | 0.51163
| 5 | 8 |  |  | 0.27119 | -1.3049 | 0.21311
| 3 | 22 |  |  | 0.33333 | -1.0986 | 0.21296
| 8 | 34 |  |  | 0.40541 | -0.90287 | 0.26471
| 7 | 26 |  |  | 0.34545 | -1.0629 | 0.5232
| 4 | 6 |  |  | 0.16774 | -1.7853 | 0.36957
| 10 | 33 |  |  | 0.18519 | -1.6864 | 0.30909
| 14 | 38 |  |  | 0.18708 | -1.6762 | 0.21519
| 0 | 0 |  |  | 0.24593 | -1.4027 | 0.37643
| 9 | 51 |  |  | 0.26988 | -1.3098 | 0.74074
| 22 | 178 |  |  | 0.92806 | -0.074662 | 0.18182
| 6 | 38 |  |  | 0.16216 | -1.8192 | 0.14433
| 16 | 102 |  |  | 0.19737 | -1.6227 | 0.12338
| 6 | 43 |  |  | 0.22963 | -1.4713 | 0.10215
| 5 | 22 |  |  | 0.29167 | -1.2321 | 0.1371
| 0 | 7 |  |  | 0.19118 | -1.6546 | 0.27941
| 3 | 14 |  |  | 0.24 | -1.4271 | 0.28049
| 6 | 19 |  |  | 0.35772 | -1.028 | 0.27119
| 4 | 29 |  |  | 0.35802 | -1.0272 | 0.33333
| 5 | 20 |  |  | 0.29204 | -1.2309 | 0.40541
| 8 | 38 |  |  | 0.29167 | -1.2321 | 0.34545
| 174 | 554 |  |  | 0.37209 | -0.98861 | 1.2581
| 1 | 0 |  |  | 0.43137 | -0.84078 | 0.16774
| 83 | 368 |  |  | 0.1873 | -1.675 | 2.8824
| 245 | 923 |  |  | 0.20037 | -1.6076 | 0.18519
| 294 | 1082 |  |  | 0.22222 | -1.5041 | 0.18708
| 815 | 2602 |  |  | 0.56757 | -0.5664 | 0.24593
| 71 | 390 |  |  | 0.37629 | -0.9774 | 0.26988
| 14 | 73 |  |  | 0.2381 | -1.4351 | 0.92806
| 7 | 53 |  |  | 0.41295 | -0.88444 | 0.16216
| 19 | 152 |  |  | 0.7 | -0.35667 | 0.19737
| 11 | 60 |  |  | 0.35849 | -1.0259 | 0.22963
| 16 | 101 |  |  | 0.4 | -0.91629 | 0.29167
| 28 | 144 |  |  | 0.208 | -1.5702 | 0.19118
| 3 | 15 |  |  | 0.36842 | -0.99853 | 1.0588
| 4 | 16 |  |  | 0.24675 | -1.3994 | 0.24
| 3 | 43 |  |  | 0.56667 | -0.56798 | 0.35772
| 3 | 27 |  |  | 0.52 | -0.65393 | 0.35802
| 4 | 2 |  |  | 0.28889 | -1.2417 | 0.29204
| 3 | 21 |  |  | 0.33333 | -1.0986 | 0.29167
| 5 | 28 |  |  | 0.19481 | -1.6358 | 0.37209
| 8 | 37 |  |  | 0.56 | -0.57982 | 0.43137
| 55 | 34 |  |  | 0.36585 | -1.0055 | 0.1873
| 9 | 38 |  |  | 0.2125 | -1.5488 | 0.20037
| 10 | 43 |  |  | 0.33591 | -1.0909 | 0.22222
| 10 | 43 |  |  | 0.20419 | -1.5887 | 0.56757
| 13 | 37 |  |  | 0.28713 | -1.2478 | 0.37629
| 7 | 56 |  |  | 0.26 | -1.3471 | 0.2381
| 6 | 31 |  |  | 0.42308 | -0.8602 | 0.41295
| 16 | 81 |  |  | 0.27027 | -1.3083 | 0.7
| 13 | 60 |  |  | 0.34483 | -1.0647 | 0.35849
| 2 | 11 |  |  | 0.27119 | -1.3049 | 0.4
| 0 | 5 |  |  | 0.36765 | -1.0006 | 0.208
| 3 | 12 |  |  | 0.34 | -1.0788 | 0.36842
| 0 | 18 |  |  | 0.38776 | -0.94738 | 0.24675
| 3 | 17 |  |  | 0.15116 | -1.8894 | 0.56667
| 7 | 38 |  |  | 0.26667 | -1.3218 | 1.4167
| 8 | 39 |  |  | 0.20435 | -1.5879 | 0.52
| 4 | 29 |  |  | 0.59756 | -0.5149 | 0.28889
| 11 | 76 |  |  | 0.15476 | -1.8659 | 0.33333
| 19 | 158 |  |  | 0.22517 | -1.4909 | 0.19481
| 12 | 98 |  |  | 0.21053 | -1.5581 | 0.56
| 18 | 117 |  |  | 0.32692 | -1.118 | 0.36585
| 5 | 44 |  |  | 0.13684 | -1.9889 | 0.2125
| 35 | 35 |  |  | 0.45098 | -0.79633 | 1.2414
| 0 | 9 |  |  | 0.55172 | -0.59471 | 1
| 4 | 26 |  |  | 0.24324 | -1.4137 | 0.33591
| 4 | 28 |  |  | 0.2342 | -1.4516 | 0.20419
| 2 | 30 |  |  | 0.21192 | -1.5515 | 0.28713
| 1 | 1 |  |  | 0.28462 | -1.2566 | 0.26
| 3 | 16 |  |  | 0.19595 | -1.6299 | 0.42308
| 2 | 15 |  |  | 0.49612 | -0.70093 | 0.27027
| 3731 | 149 |  |  | 0.40506 | -0.90371 | 0.34483
| 4434 | 163 |  |  | 0.35754 | -1.0285 | 0.27119
| 8343 | 211 |  |  | 0.53165 | -0.63178 | 0.36765
| 10526 | 274 |  |  | 0.44167 | -0.8172 | 0.34
| 13424 | 360 |  |  | 0.23581 | -1.4447 | 0.38776
| 6 | 36 |  |  | 0.22063 | -1.5113 | 0.15116
| 9 | 56 |  |  | 0.023225 | -3.7625 | 0.26667
| 10 | 48 |  |  | 0.27072 | -1.3067 | 0.20435
| 9 | 30 |  |  | 0.275 | -1.291 | 0.59756
| 16 | 80 |  |  | 0.33544 | -1.0923 | 0.15476
| 10 | 58 |  |  | 0.15498 | -1.8644 | 0.22517
| 14 | 62 |  |  | 0.42618 | -0.85288 | 0.21053
| 17 | 43 |  |  | 0.31959 | -1.1407 | 0.32692
| 8 | 35 |  |  | 0.32298 | -1.1302 | 1.3103
| 0 | 0 |  |  | 0.32192 | -1.1335 | 0.13684
| 3 | 9 |  |  | 0.84091 | -0.17327 | 37.9375
| 17 | 51 |  |  | 0.38462 | -0.95551 | 0.45098
| 4 | 12 |  |  | 0.34615 | -1.0609 | 6.375
| 20 | 119 |  |  | 0.22115 | -1.5089 | 0.55172
| 15 | 102 |  |  | 0.54902 | -0.59962 | 0.24324
| 11 | 50 |  |  | 0.34884 | -1.0531 | 0.2342
| 22 | 164 |  |  | 0.25 | -1.3863 | 0.21192
| 11 | 82 |  |  | 0.26 | -1.3471 | 0.28462
| 7 | 50 |  |  | 0.21212 | -1.5506 | 0.19595
| 10 | 65 |  |  | 0.26531 | -1.3269 | 0.49612
| 8 | 50 |  |  | 0.5 | -0.69315 | 0.40506
| 6 | 68 |  |  | 0.24444 | -1.4088 | 0.35754
| 22 | 104 |  |  | 0.25758 | -1.3564 | 0.53165
| 10 | 66 |  |  | 0.32222 | -1.1325 | 2.7692
| 4 | 22 |  |  | 0.22581 | -1.4881 | 0.44167
| 3 | 20 |  |  | 0.23457 | -1.45 | 0.23581
| 9 | 63 |  |  | 0.31126 | -1.1671 | 0.22063
| 8 | 36 |  |  | 0.35 | -1.0498 | 1.1667
| 13 | 67 |  |  | 0.30769 | -1.1787 | 0.023225
| 11 | 37 |  |  |  |  | 0.27072
| 5 | 30 |  |  |  |  | 0.275
| 12 | 42 |  |  |  |  | 0.33544
| 27 | 37 |  |  |  |  | 0.15498
| 3969 | 263 |  |  |  |  | 114.6016
| 2 | 9 |  |  |  |  | 0.42618
| 2 | 17 |  |  |  |  | 0.31959
| 0 | 0 |  |  |  |  | 0.32298
| 1 | 0 |  |  |  |  | 0.32192
| 1 | 9 |  |  |  |  | 0.84091
| 2 | 10 |  |  |  |  | 0.38462
| 1 | 6 |  |  |  |  | 0.34615
| 3 | 4 |  |  |  |  | 0.22115
| 8 | 56 |  |  |  |  | 0.54902
| 7 | 53 |  |  |  |  | 0.34884
| 8 | 57 |  |  |  |  | 0.25
| 23 | 73 |  |  |  |  | 0.26
| 8 | 64 |  |  |  |  | 0.21212
| 14 | 68 |  |  |  |  | 0.26531
| 5 | 40 |  |  |  |  | 0.5
| 18 | 44 |  |  |  |  | 0.24444
| 7 | 46 |  |  |  |  | 0.25758
| 18 | 99 |  |  |  |  | 0.32222
| 26 | 146 |  |  |  |  | 0.22581
| 11 | 35 |  |  |  |  | 0.23457
| 19 | 90 |  |  |  |  | 0.31126
| 9 | 46 |  |  |  |  | 0.35
| 10 | 42 |  |  |  |  | 0.30769
| 0 | 0
| 6 | 34
| 6 | 22
| 5 | 39
| 9 | 49
| 0 | 28
| 5 | 61
| 3 | 21
| 2 | 2
| 2 | 6
| 2 | 4
| 0 | 4
| 10 | 14
| 8 | 12
| 3 | 9
| 2 | 4
| 0 | 0
| 3 | 3
| 1 | 22
| 19 | 120
| 15 | 118
| 8 | 86
| 17 | 98
| 0 | 5
| 5 | 49
| 3 | 13
| 2 | 14
| 1 | 0
| 0 | 0
| 7709 | 222
| 8733 | 301
| 12346 | 426
| 14 | 7
| 0 | 0
| 32 | 45
| 11 | 23
| 17 | 76
| 22 | 93
| 1 | 0
| 6 | 42
| 7 | 9
| 11 | 41
| 4 | 14
| 5 | 31
| 4 | 0
| 6 | 28
| 11833 | 374
| 8504 | 243
| 9 | 73
| 10 | 43
| 10 | 54
| 13 | 61
| 14 | 108
| 10 | 40
| 14 | 68
| 9 | 55
| 7 | 47
| 8 | 23
| 6 | 33
| 9 | 45
| 6 | 36
| 6 | 0
| 137 | 388
| 5 | 5
| 3 | 14
| 17 | 46
| 8 | 35
| 11 | 39
| 8 | 48
| 9 | 40
| 14 | 55
| 17 | 79
| 12 | 43
| 4 | 11
| 4 | 15
| 6 | 25
| 4 | 0
| 4 | 24
| 6 | 25
| 7 | 24
| 308 | 1315
| 14 | 27
| 14 | 77
| 14 | 97
| 19 | 154
| 19 | 186
| 17 | 124
| 16 | 68
| 7 | 37
| 8 | 49
| 14 | 82
| 10 | 59
| 9 | 39
| 8 | 37
| 14 | 55
| 6 | 33
| 31 | 31
| 5 | 34
| 5 | 33
| 6 | 0
| 2 | 15
| 18 | 155
| 1 | 1
| 0 | 2
| 0 | 0
| 0 | 0
| 6 | 41
| 3 | 28
| 0 | 24
| 20 | 17
| 5 | 38
| 2 | 0
| 0 | 10
| 10 | 81
| 1 | 5
| 2 | 3
| 0 | 7
| 0 | 0
| 0 | 0
| 32 | 0
| 36 | 0
| 1 | 0
| 7 | 0
| 70 | 0
| 25 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 4 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 94 | 743
| 187 | 1476
| 362 | 2716
| 104 | 139
| 48 | 333
| 7 | 44
| 15 | 76
| 10 | 67
| 8 | 59
| 21 | 135
| 7 | 48
| 12 | 68
| 14 | 17
| 15 | 75
| 12 | 46
| 33 | 123
| 11 | 252
| 24 | 81
| 27 | 113
| 16 | 72
| 29 | 86
| 3 | 0
| 60 | 153
| 20 | 0
| 308 | 1890
| 279 | 1612
| 31 | 153
| 55 | 148
| 58 | 194
| 76 | 441
| 97 | 448
| 65 | 220
| 40 | 1
| 16 | 53
| 5 | 19
| 5 | 21
| 6 | 8
| 12 | 35
| 12 | 13
| 0 | 0
| 1 | 18
| 13 | 125
| 9 | 66
| 0 | 3
| 2 | 5
| 0 | 8
| 0 | 9
| 11 | 89
| 15 | 57
| 14 | 77
| 8 | 68
| 11 | 30
| 12 | 12
| 0 | 0
| 0 | 0
| 8 | 25
| 1 | 0
| 4 | 19
| 3 | 24
| 5 | 26
| 1 | 0
| 2 | 0
| 0 | 0
| 11 | 45
| 4 | 21
| 7 | 36
| 7 | 23
| 4 | 22
| 0 | 14
| 0 | 0
| 0 | 4
| 0 | 8
| 3 | 13
| 0 | 14
| 0 | 8
| 2 | 12
| 9 | 50
| 8 | 37
| 9 | 53
| 9 | 60
| 3 | 10
| 6 | 47
| 7 | 53
| 8 | 42
| 2 | 22
| 4 | 36
| 10 | 77
| 6 | 36
| 5 | 32
| 8 | 36
| 10 | 13
| 2 | 4
| 3 | 24
| 0 | 18
| 11 | 25
| 2 | 36
| 0 | 1
| 3 | 16
| 0 | 1
| 0 | 0
| 2 | 0
| 2 | 11
| 3 | 11
| 0 | 0
| 3 | 18
| 14 | 41
| 7 | 54
| 8 | 80
| 6 | 46
| 0 | 7
| 4 | 24
| 7 | 13
| 4 | 11
| 2 | 2
| 0 | 0
| 8 | 68
| 6 | 36
| 8 | 43
| 4 | 36
| 4 | 42
| 7 | 27
| 2 | 12
| 3 | 16
| 0 | 0
| 2 | 21
| 4 | 36
| 4 | 38
| 4 | 29
| 5 | 42
| 26 | 36
| 3 | 12
| 0 | 0
| 3 | 0
| 42 | 259
| 25 | 191
| 28 | 202
| 22 | 150
| 6 | 37
| 9 | 41
| 19 | 52
| 7 | 32
| 5 | 22
| 5 | 20
| 16 | 74
| 5 | 29
| 15 | 58
| 10 | 71
| 10 | 62
| 13 | 59
| 6 | 30
| 17 | 68
| 9 | 50
| 7 | 45
| 11 | 49
| 13 | 86
| 8 | 57
| 20 | 75
| 8 | 40
| 6 | 28
| 0 | 3
| 6 | 32
| 4 | 21
| 6 | 32
| 4 | 1
| 69 | 460
| 0 | 0
| 62 | 5
| 42 | 82
| 9 | 43
| 13 | 84
| 19 | 151
| 12 | 95
| 11 | 70
| 8 | 67
| 10 | 52
| 7 | 45
| 6 | 40
| 7 | 29
| 0 | 6
| 0 | 9
| 1 | 0
| 2 | 9
| 6 | 40
| 5 | 35
| 6 | 46
| 4 | 26
| 31 | 29
| 8 | 41
| 0 | 1
| 0 | 0
| 0 | 0
| 0 | 4
| 6 | 0
| 3 | 0
| 13 | 95
| 5 | 30
| 274 | 16
| 20 | 51
| 293 | 72
| 4 | 29
| 6 | 29
| 0 | 5
| 2 | 7
| 2 | 10
| 1 | 1
| 1 | 0
| 2 | 47
| 9 | 6
| 57 | 259
| 58 | 269
| 32 | 151
| 29 | 130
| 25 | 148
| 28 | 129
| 49 | 158
| 49 | 179
| 216 | 553
| 29 | 13
| 41 | 120
| 138 | 793
| 222 | 1328
| 10 | 57
| 4 | 17
| 3 | 11
| 3 | 0
| 0 | 21
| 2 | 14
| 4 | 16
| 8 | 12
| 2 | 2
| 0 | 0
| 0 | 0
| 45 | 2239
| 36 | 181
| 38 | 200
| 28 | 158
| 30 | 271
| 42577 | 630
| 110 | 359
| 44 | 194
| 40 | 161
| 36 | 146
| 7 | 25
| 4 | 45
| 6 | 35
| 8 | 39
| 5 | 27
| 4 | 30
| 0 | 8
| 2 | 6
| 0 | 8
| 3 | 22
| 0 | 8
| 0 | 4
| 11 | 47
| 7 | 45
| 8 | 50
| 7 | 47
| 0 | 26
| 5 | 24
| 0 | 0
| 1 | 8
| 2 | 6
| 0 | 4
| 2 | 8
| 9 | 58
| 8 | 49
| 8 | 48
| 5 | 38
| 29 | 44
| 4 | 37
| 0 | 14
| 3 | 6
| 6 | 5
| 4 | 14
| 6 | 20
| 5 | 22
| 4 | 12
| 12 | 86
| 6 | 32
| 9 | 45
| 5 | 43
| 6 | 73
| 5 | 43
| 0 | 8
| 1 | 21
| 3 | 7
| 2 | 1
| 0 | 0
| 7 | 37
| 2 | 12
| 13 | 39
| 4 | 19
| 2 | 24
| 2 | 12
| 2 | 18
| 5 | 23
| 12 | 52
| 6 | 43
| 18 | 104
| 20 | 51
| 0 | 0
| 3 | 11
| 11 | 56
| 15 | 43
| 6 | 58
| 11 | 56
| 4 | 50
| 13 | 50
| 4 | 34
| 0 | 6
| 4 | 13
| 0 | 0
| 4 | 12
| 3 | 8
| 7 | 7
| 23 | 1
| 14 | 66
| 6 | 45
| 6 | 45
| 3 | 30
| 7 | 49
| 5 | 31
| 5 | 40
| 3 | 20
| 3 | 25
| 13 | 36
| 3 | 28
| 42 | 180
| 12 | 58
| 12 | 63
| 13 | 66
| 17 | 90
| 7 | 0
| 9 | 62
| 11 | 81
| 6 | 36
| 3 | 1
| 4 | 28
| 39 | 151
| 8 | 31
| 9 | 44
| 10 | 34
| 13 | 60
| 7 | 0
| 7 | 58
| 10 | 52
| 3 | 30
| 3 | 20
| 0 | 0
Run Gas Calculations
Run Gas Ratio Calculations